## Slide 1: Headline Verdana Bold
Final Report
Suggesting Roadmap for Achieving Net Surplus Energy Status for SECL by FY 2025-26
Dec-2022
Notes: To be picked from https://consulting.deloitteresources.com/brand/Pages/Imagery.aspx
https://brandspace.deloitte.com/content/index/guid/image_library?search_term=&list_size=25&assettag%5B16%5D%5B%5D=43&assettag%5B19%5D%5B%5D=50

## Slide 2
Disclaimer
  This Report has been prepared by Deloitte Touche Tohmatsu India LLP (“DTTILLP”) in accordance with the Work Order No. SECL/BSP/GM(NI/NT)/2022/25 dated 20th April 2022 issued by South Eastern Coalfields Limited (“Client”) and is subject to the scope of work, approach, assumptions and other conditions mentioned in the Work Order and the conditions mentioned in this Report.
This Report and the information contained herein has been prepared by DTTILLP solely for the benefit of the Client and is intended for use by the Client solely. The Client shall not use this Report for any other purpose and in particular shall not use this Report in connection with the business decisions of any third party and for advisement purposes.
  This Report contains analyses that are intended to provide high-level information on the subject and are not an exhaustive treatment of the subject. The analyses in the Report are limited by the scope of work, the time allocated, information made available to DTTILLP or collected by DTTILLP and are heavily dependent upon the assumptions specified in the Work Order and this Report. This Report is not intended to be relied upon as a sole basis for any decision and the Client should take decisions only after seeking professional advice and after carrying out their own due diligence procedures, detailed analysis to ensure that they are making an informed decision. This Report is not and should not be construed in any way as giving any investment advice or any recommendations by DTTILLP to the Client or any other party. The Client shall be solely responsible for any and all decisions (including the implications thereof) made by the Client on the basis of this Report.
  This Report has been prepared on the basis of information made available, obtained and collected by DTTILLP in relation to this engagement from the Client as well as from various other primary and secondary sources. It shall be noted that information and data pertaining to the Client that is contained in this Report, has been compiled /incorporated on an “as-is” basis, completely and solely from the information provided by the Client. The sources of any material information (except that collected from primary sources) used in the Report has been mentioned or cited herein. The information obtained and collected from the Client and various other primary and secondary sources has been used on an “as-is” basis without any independent verification by DTTILLP. DTTILLP shall not be held responsible for any error or omissions, or for the results obtained from the use of this information; and DTTILLP provides no assurance regarding the accuracy, timeliness, adequacy, comprehensiveness and/ or completeness of such information and provides no warranty of any kind, express or implied, including, but not limited to warranties of performance and fitness for a particular purpose. DTTILLP shall not be liable for any losses and damages arising as a result of any inaccuracy or inadequacy or incomprehensiveness or incompleteness of such information.
  DTTILLP’s procedures did not constitute an audit. Accordingly, DTTILLP has not expressed any opinion on the past and current financial statements.
  This Report is solely for the use of the Client, as per the terms of the Contract. The Report is issued on the basis that this Report or any information derived therefrom, shall not be shared with or provided to any third party without the prior written consent of DTTILLP.

## Slide 3: Contents
1
Introduction
3
Assessment of Solar Capacity
4
Financial Assessment of various Business Models for Self-Consumption
5
Comparison of Risks of Different Models
6
Land Assessment
2
Business Models Envisaged
7
Procedural Requirements
8
Assessment of Potential Avenues for Sale of Surplus Solar Energy
9
Evaluation Summary
Conclusion and Way Forward
Annexures
10
11

## Slide 4: Introduction

## Slide 5
For Administrative purposes, SECL command centres are divided in 14 areas distributed in 4 clusters/ coalfields
SECL is a wholly-owned subsidiary of Coal India Limited and a Mini-Ratna Company. It is the largest coal producing company of India. The coal mines of SECL are spread across two states namely Chhattisgarh and Madhya Pradesh. SECL operates 67 coal mines , of which 41 coal mines lies in Chhattisgarh State, while rest 26 coal mines are situated in Madhya Pradesh state. Out of the 67 coal mines of SECL, 46 mines are worked by underground method of mining while rest 21 mines are Opencast mines. Along with this, SECL is committed towards operational aspect of coal carbonization plant of Dankuni coal complex. The Dankuni coal Complex at Dankuni, West Bengal has been given on lease basis by CIL..
About SECL
Chart: 
| 1st Qtr | 2nd Qtr
Sales | 68 | 32
Chhattisgarh
132
Mt
Chart: 
| 1st Qtr | 2nd Qtr
Sales | 68 | 32
722
MU
SECL’s 41 mines in CG produced 132.35 MT coal in FY22
SECL mines in CG consumed 721.5 MU electricity in FY22
Chart: 
| 1st Qtr | 2nd Qtr
Sales | 68 | 32
Madhya Pradesh
10
Mt
Chart: 
| 1st Qtr | 2nd Qtr
Sales | 68 | 32
263
MU
SECL has 26 mines in MP producing 10.17 Mt Coal in FY22
SECL mines in MP consumed 263 MU electricity in FY22
Central India Coalfields | Korba Coalfields | Mand-Raigarh Coalfields | Coal Carbonization Plant
1. Chirimiri 2. Baikunthpur 3. Bisrampur 4. Hasdeo 5. Bhatgaon 6. Jamuna & Kotma 7. Sohagpur 8. Johilla | 1. Korba 2. Kusmunda 3. Dipka 4. Gevra | 1. Raigarh | 1. Dankuni Coal Complex, Dankuni, West Bengal.

## Slide 6
Project Background
MoC mandate to CIL
MoC mandated CIL to take up de-carbonization initiatives
CIL Directives
CIL directed its subsidiaries to come up with a plan to implement solar in their portfolio
Need to Identify the Business Options
SECL now wants to assess various existing market practices like, capex-based, BOO-based, or government-scheme based models to identify the most suitable model
500 GW RE by FY30
GoI has taken a target of implementing Renewables and propelling it up
Existing Programs
SECL already is in the process to implement 142.3 MW solar projects via 100 MW BOOT model through SECI, 40 MW on EPC based in own land and 2.3 MW of rooftop solar on non-residential buildings
Deloitte Report
Analysis by Deloitte based on financial, procedural and risk assessment on the basis of the data provided by SECL, market trends, stakeholder interactions
CIL Target
CIL targets 3 GW of solar capacity
Remaining 600 MW
SECL internally assessed remaining capacity required to meet the Net-Surplus target is 600 MW
280-300 GW out of 500 GW targeted to be achieved from Solar
SECL Targets to become Net-Surplus with solar by FY26
Deloitte appointed by SECL

## Slide 7
Process Adopted by Deloitte
Assessment of Solar Capacity
Solar generation capacity is estimated based on the electricity consumption projection and the CUF envisaged
Estimation of Financial Savings
Landed costs are drawn (metering point-wise)
SECL’s future electricity consumption (metering point-wise) is estimated based on historical electricity consumption, coal production and projected coal production
Open access losses are assessed, and total required installed capacity and energy is estimated after accounting the losses
Capacities required for the various business models are estimated
Savings are estimated compared to the landed cost and estimated Energy Charge trajectory
Metering point-wise discom energy charge trajectory is assessed
Open access Regulatory charges are assessed and projected
Costs of generation are estimated based on certain set of assumptions
Business Models
Business models being envisaged are identified
Mapping of the possible business models for self-consumption (captive) and surplus sale (non-captive) are done
Other Assessment
Availability of land parcels with SECL vis-à-vis requirement is assessed
Procedural requirements are examined based on study of regulations
Potential avenues for sale of surplus solar energy are evaluated
Business models (for self-consumption) and Options for surplus power sale are evaluated based on various metrics
Based on above evaluation, best-fit models / options have been identified

## Slide 8
Chart: 
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 1 | 3 | 1 | 1
Triangulation
Secondary
Interactions with SECL
Interactions with Industry
Secondary sources
To understand the internal processes, electricity demand and trajectories,
coal production projection
To understand power and RE market dynamics, surplus power potential customers, channel partners, & expectations from stakeholders
To understand the regulatory landscape, charges, mechanism, trajectories etc. backed-up with data
Industry
Organization (SECL)
Team interacted with SECL key stakeholders, accountable persons
Interactions via Video / Tele – conferencing and Visit to SECL
Data provided by SECL
Team interacted with EPC players, Owner’s Engineers-cum-PMC players, regulators, discoms, market players, power exchange etc., as and when required
SERCs and Discoms websites
Public Domain regulations, notifications, policies and other relevant information
Market information sources, publications, databases etc.
Data from relevant third party data sources
Our Approach-The Interactions
Notes: Across each of the two approach elements, we have broken down the major workstreams into outcome oriented ‘activities. Each of the activity in itself culminating into an engagement milestone deliverable

## Slide 9
The Transmission Losses of CG and MP are as follows and the same is estimated to remain for project period
  CG (T&D Loss combined) for intra-state generation and consumption: 6%
  CG transmission loss (for multi-state drawl and consumption): 3%
  CG distribution loss (for multi-state drawl and consumption): 6%
  MP Transmission Loss: 4.5%
  MP Distribution Loss: 5.1%
  ISTS loss: 3.25 %
  (all taken from Regulatory Orders by CSERC/ MPERC)
CUF: 26.50% (calculated from SECI’s presentation to SECL and SECI’s assessment for PFS and normalizing the same based on overloading)
Solar Capacity Estimation is based on FY26 projected consumption details and the same has been considered for future years
Interest Rate for Debt Financing: 6% interest rate (as discovered by CIL during GUVNL 100 MW tender) plus 40 basis points for repo rate correction twice, and rounding off i.e. a total of 7.00% interest rate
Debt: Equity Ratio: Three (3) scenarios has been taken, as follows:
  80:20 (most commonly practiced in the sector)
  50:50
  0:100 (complete equity funded project)
6. Capex Scenarios
  The module charge has been derived based on the cell cost, glass cost (source: pvinfolink) and copper, aluminium prices (source: LME)
  Tolling charge has been derived from primary industry interactions and intelligence
  Other BOS charges derived from the proportionate distribution of cost as discovered during CIL’s tendering for GUVNL 100 MW and MCL 50 MW
  The total base Capex (excluding land) is coming to Rs. 6.35 Cr/MW
  Also, another capex scenario is obtained from CIL’s experience of bidding for EPC selection, a scenario of 10% reduction in the cost is taken
7. ISTS Charges
  If ISTS charge is not waived, then the charge is estimated to be increasing in the CAGR of recent trend from the baseline value of Rs. 3.15/unit in FY22
8. Solar Generation Hours
  Solar plant is expected to generate from 8 am to 4 pm, i.e. 8 hours a day (average for entire year, considering shorter winter days, less generation during monsoons etc.). The corresponding solar capacity has been considered for captive consumption of SECL.
9. Land
  Lan price: Rs. 10 lakhs/acre (Chhattisgarh), Rs. 12 lakhs/ acre (Madhya Pradesh)
  Lan requirement: 4 acre/ MW (industry norms)
Key Assumptions

## Slide 10
Information Sought by Deloitte
Energy Consumption | Metering point-wise, voltage-wise energy consumption details for last 6 years Metering point-wise, voltage-wise energy consumption projection for next 5 years, if available Metering-point-wise, voltage-wise average load for last 6 years Latest years Hourly data of energy consumption of multiple metering points for 3 seasons-summer, winter and monsoon Some sample electric bills of last 5 years for both the discoms from which SECL is drawing power
Existing/ Upcoming Solar Plants of SECL | Capacities, status, expected date of commissioning of existing/ upcoming solar PV/ rooftop and the expected generation for next 25 years Existing solar plant’s recent year’s hourly data for multiple seasons, if any.
Coal Production Details | Last 6 years’ yearly coal production details, segregated state-wise (i.e. MP or CG) Next 5 years’ yearly coal production details, segregated state-wise (i.e. MP or CG)
Others | Any other relevant information on connectivity etc.
Deloitte prepared the following Information Requirement List for SECL

## Slide 11
Basis of the Report
Data Provided by SECL | Metering point-wise, voltage-wise energy consumption details for last 6 years Metering point-wise, voltage-wise energy consumption projection for next 5 years, if available Metering-point-wise, voltage-wise average load for last 6 years Latest years Hourly data of energy consumption of multiple metering points for 3 seasons-summer, winter and monsoon Sample electric bills of last 5 years for both the discoms from which SECL is drawing power Capacities, status, expected date of commissioning of existing/ upcoming solar PV/ rooftop and the expected generation for next 25 years Last 6 years’ yearly coal production details, segregated state-wise (i.e. MP or CG) Next 5 years’ yearly coal production details, segregated state-wise (i.e. MP or CG) Land Parcel Details of SECL Power Drawl diagrams of various areas of SECL
Information From State Utilities/ SERCs/ Nodal Agencies/ other Stakeholders | Understanding the regulatory provisions for selling of surplus power Idea of regulatory provisions and restrictions/ limitations of connectivity for captive/ non-captive solar power plants Regulatory charges trends and their outlook Discom’s appetite for purchasing surplus power Available evacuation capacities and sub-stations of discoms and transcos for potential evacuation route Energy Banking provisions of respective states Processes and compliances for setting up a solar plant and the approvals required Available benefits/ supports that may be provided by the state solar development nodal bodies like CREDA Existing power scenario of the state and outlook
Secondary sources | Respective Regulations and tariff orders of Chhattisgarh and Madhya Pradesh related to energy charges, open access charges and their waiver, energy banking, energy sales etc. Orders and circulars related to ISTS charges, its waivers, government schemes like CPSU scheme etc. Solar module and its components pricing from Pvinfolink, LME etc. and their trajectories Information on the capex scenarios from EPC players
Deloitte prepared the Report based on following Information gathered during primary and secondary interactions

## Slide 12: Business Models Envisaged

## Slide 13
Models envisaged for achieving Net-Surplus status
MODELS
Models for Self-Consumption
Models for Surplus Sale of Solar Power
Establishment of solar project in capex mode (Captive):
SECL will incur capex for the project and may deploy EPC contractor for setting up the project
Based on availability of suitable land, project can be set up in:
own land of SECL, and/or
other land
Based on availability of suitable land, project can be situated in Chhattisgarh and/or Madhya Pradesh
Purchase of solar power through BOO-route:
SECL will invite bids for selection of developer through tariff-based competitive bidding for development of solar project in BOO-route
Project can be situated in Chhattisgarh and/or Madhya Pradesh (project situated in any other state will attract ISTS charges)
Purchase of solar power under GOI-scheme (e.g., CPSU Scheme Phase-II):
SECL may explore availability of un-tied capacity from awarded solar projects under CPSU Scheme Phase-II tenders
CPSU Scheme Phase-II is explained in Annexure-1
Establishment of solar project in capex mode:
SECL will incur capex for the project and may deploy EPC contractor for setting up the project
Based on availability of suitable land, project can be set up in:
own land of SECL, and/or
other land
Based on availability of suitable land, project can be situated in Chhattisgarh and/or Madhya Pradesh
Various avenues for sale of surplus solar power:
Sale to Discoms of Chhattisgarh or Madhya Pradesh
Energy Banking
Sale through Power Exchanges
Sale to Power Traders
Sale to Open Access Consumers
Sale of Renewable Energy Certificates (REC)

## Slide 14
Pictorial representation of Business Models for Self-Consumption
SECL
Capex
Power
Model 1: Capex Model (Captive)
Solar Plant*
Consumption Points
SECL Ownership
EPC cum O&M Player
Payment as per bidding discovery
PMC-cum-Owner’s Engg
Payment as per agreement after selection through bidding
Planning & Design, check, QA-QC, PMC
Bank/FI
Debt Financing
SECL
Capex
Power
Model 2: BOO Model (PPA)
Solar Plant
Consumption Points
SECL Ownership
Solar Project Developer
Payment as per discovered Tariff through bidding and corresponding PPA
Model 3: Government Scheme based PPA
SECL
Capex
Power
Solar Plant
Consumption Points
SECL Ownership
Solar Project Developer
Payment as per discovered Tariff through bidding and corresponding PPA
Capital Subsidy and any other Waiver from Government Schemes like CPSU scheme etc.
Government Entity
Ownership, EPC, O&M Responsibilities
Ownership, EPC, O&M Responsibilities
*Location of the Plant
Option A: Own Land
Option B: Others’ Land

## Slide 15
For Captive and BOO, three operational models are envisaged, while for Government scheme option, CG and MP consumptions are independent to one another but all the state charges are applicable:
Option 1: Entire Plant Capacity is in Chhattisgarh (CG) and Power is drawn to MP and CG metering Points using ISTS, STU and Discom Network
Option 2: Entire Plant Capacity is in Madhya Pradesh (MP) and Power is drawn to MP and CG metering Points using ISTS, STU and Discom Network
Option 3: Solar Plants are located in both CG and MP, based on the demands of the metering points located in respective states and no inter-state transmission
Options
Business Models for Self-Consumption have been segregated in various options based on plant location
Option 1
Option 2
Option 3
Combined Model
Power
Power
Power
Power
Power
Power
Generation Point
Consumption Point
Power Flow
Captive Model and BOO Model
Government Scheme-PPA Model
Entire Capacity in CG
Drawl in CG & MP
Power
Power
Entire Capacity in MP
Drawl in CG & MP
CG required capacity in CG and drawl in CG
MP required capacity in MP and drawl in MP
Generation anywhere in India
Drawl at MP and CG based on their requirement

## Slide 16
Pictorial representation of Business Models for Surplus Sale
SECL
Capex
Power
Capex Model
Solar Plant*
Sale options
SECL Ownership
EPC cum O&M Player
Payment as per bidding discovery
PMC-cum-Owner’s Engg
Payment as per agreement after selection through bidding
Planning & Design, check, QA-QC, PMC
Bank/FI
Debt Financing
*Location of the Plant
Option A: Own Land
Option B: Others’ Land
Sale to CG / MP Discoms
Energy Banking
Sale through Exchanges
Sale to Traders
Sale to Open Access Consumers
Sale of Renewable Energy Certificates
Plant in CG
Plant in MP
Plants in CG and MP
Power
Power
Power
Power
Generation Point
Location options
Sale to beneficiaries
Sale to beneficiaries
Sale to beneficiaries
Power Flow

## Slide 17: Assessment of Solar Capacity

## Slide 18
Coal Production by SECL – Historical and Projected
SECL produced almost 143 Mt in FY22 and as per SECL’s projection, the production is expected to rise to 269 Mt by FY26
Total (SECL)
Historical Coal Production by SECL (in Mt)
SECL’s Projected Coal Production (in Mt)
Key Takeaways
The expected production of SECL is going to be almost 1.7X in next 5 years
Most of the production, i.e., almost 93% is coming from Chhattisgarh mines and the trend is expected to be continued till FY26
Gevra, Dipka, Kusmunda and Raigarh accounts for almost 83% of the total production, which is not expected to change in near future
Source: SECL
Chart: 
| FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27
Baikunthpur (CG) | 2.23 | 2.52 | 2.59 | 2.53 | 2.44 | 2.07 | 2.96 | 3.68 | 4.23 | 4.31 | 4.4
Bhatgaon (CG) | 2.93 | 3.23 | 3.17 | 3.19 | 3.76 | 2.63 | 3.9 | 4.84 | 5.56 | 5.67 | 5.79
Bishrampur (CG) | 2.69 | 1.69 | 0.99 | 0.57 | 0.39 | 0.29 | 1.4 | 1.73 | 1.99 | 2.03 | 2.07
Chirimiri (CG) | 3.2 | 3.38 | 2.96 | 2.47 | 1.99 | 2.46 | 3.41 | 4.24 | 4.86 | 4.96 | 5.07
Dipka (CG) | 31 | 34.35 | 35 | 25.18 | 34.35 | 34.37 | 40.11 | 49.84 | 57.21 | 58.33 | 59.6
Gevra (CG) | 41 | 41.43 | 42.25 | 45 | 40.57 | 41.45 | 51.94 | 64.54 | 74.09 | 75.55 | 77.18
Hasdeo (CG) | 0.25 | 0.18 | 0.17 | 0.16 | 0.14 | 0.11 | 0.21 | 0.26 | 0.3 | 0.3 | 0.31
Hasdeo (MP) | 3.27 | 2.92 | 3.2 | 2.69 | 2.05 | 2.22 | 3.22 | 3.73 | 4.68 | 4.98 | 4.45
J&K (MP) | 3.06 | 2.79 | 2.81 | 2.49 | 1.9 | 2.26 | 3.02 | 3.51 | 4.39 | 4.67 | 4.18
Johilla (MP) | 2 | 2.1 | 1.87 | 0.88 | 1.42 | 1.67 | 1.96 | 2.28 | 2.85 | 3.03 | 2.71
Korba (CG) | 5.14 | 5 | 6.33 | 6.4 | 6.2 | 7.27 | 7.49 | 9.3 | 10.68 | 10.89 | 11.12
Kusmunda (CG) | 26 | 26 | 40 | 42.33 | 37.26 | 28.9 | 41.09 | 51.05 | 58.6 | 59.75 | 61.05

## Slide 19
Electricity Consumption by SECL – historical and projected
SECL consumed approximately 988 MU electricity in FY22; Electricity consumption in FY26 is projected at 1926 MU in line with the projected coal production
Chart: 
| FY17 | FY18 | FY19 | FY20 | FY21 | FY22
Energy Consumption (MU) | 1039.95 | 998.72 | 984.73 | 997.82 | 1003.05 | 988.18
Historical Electricity Consumption Trend of SECL (in MU)
Key Takeaways
Electricity Consumption for per ton Coal Production of SECL was 6.863 kWh/tonne to 7.308 kWh/tonne over the period of FY17-FY22. The average was 6.591 kWh/tonne
The envisaged energy savings measure of SECL till FY23 only amounts to ~15 MU (details in Annexure-2) and no further energy savings is envisaged at this moment. The energy conservation plan accounts for only ~1.5% of the current electricity consumption
Therefore, the historical electricity consumption pattern is expected to be continued till FY26
Source: SECL
Chart: 
| FY23 | FY24 | FY25 | FY26
 | 1301.89 | 1589.65 | 1866.84 | 1925.52
Projected Electricity Consumption of SECL till FY26 (in MU)

## Slide 20
Assessment of Solar Capacity for Net-Surplus
For SECL to achieve Net-Surplus status by FY 26, the solar capacity of SECL for FY 26 should at least be higher than the projected electricity consumption for FY 26
Projected Electricity Consumption of SECL till FY 26 (in MU)
Key Takeaways
Solar capacity has been estimated based on the projected electricity consumption and the assumed CUF
The quantum solar electricity from the above solar capacity will be generated during the sunshine hours (assumed to be 8 hours), whereas the quantum of electricity consumption indicated above will take place over the period of 24 hours. Therefore, there will be surplus solar electricity after self-consumption by SECL.
Hence, the entire solar capacity will be utilized in two parts – (a) for self-consumption by SECL, and (b) sale of surplus solar power.
Minimum Solar Capacity required at consumption-end for Net-Surplus status of SECL till FY26 (in MW)
Chart: 
| FY23 | FY24 | FY25 | FY26
Projected MU (CG) | 931.5399 | 1137.4338 | 1335.7711 | 1377.7598
Projected MU (MP) | 362.5677 | 442.7044 | 519.8999 | 536.2425
Projected MU - Others | 7.7867 | 9.5077 | 11.1656 | 11.5166
Total SECL | 1301.8943 | 1589.6459 | 1866.8366 | 1925.5189
Chart: 
| FY23 | FY24 | FY25 | FY26
Solar MW (CG) | 401.2837 | 489.9775 | 575.4162 | 593.5038
Solar MW (MP) | 156.1849 | 190.7058 | 223.9596 | 230.9996
Total SECL | 557.4686 | 680.6833 | 799.3758 | 824.5034

## Slide 21: Assessment of Solar Capacity (at consumption-end) for Self-Consumption and Solar Capacity for Surplus Sale
The overall solar capacity can be bifurcated into capacity for self-consumption and capacity for surplus sale based on the sunshine hours, which is assumed to be 8 hours for this study
State-Wise bifurcation of Solar Capacity at consumption-end for FY 26 into (a) capacity for self-consumption and (b) capacity for surplus sale (MW)
Chart: 
| CG | MP
Sales | 594 | 231
Chart: 
| CG | MP
Sales | 198 | 77
Key Takeaways
Solar capacity for self-consumption is around 33% of the overall solar capacity. If the solar capacity is set up in Capex mode by SECL (i.e., captive power plant), then in order to fulfil the captive power plant criteria (at least 51% annual electricity consumption by captive user), the captive solar plant needs to be separated from the remaining capacity
Criteria for captive power plant are provided in Annexure-3
Total Solar Capacity Requirement for Achieving Net Surplus for FY 26 (MW)
Solar Capacity for Self-Consumption for FY 26 (MW)
Chart: 
| CG | MP
Sales | 396 | 154
Solar Capacity for surplus sale for FY 26 (MW)
+
=
Total Capacity: 825 MW
Total Capacity: 275 MW
Total Capacity: 550 MW

## Slide 22: Assessment of Captive Solar Capacities (at generation-end) for different location-options
Option 1: Entire Solar Capacity is in CG (figures in MW) | Option 2: Entire Solar Capacity is in MP (figures in MW) | Option 3: Solar Capacity in both CG and MP as per demand (figures in MW)
Chart: 
| CG | MP
in MW | 210 | 96
Chart: 
| CG | MP
in MW | 247 | 85
Chart: 
| CG | MP
in MW | 210 | 85
Solar capacities at generation-end are assessed by grossing up the solar capacities at consumption-end with applicable open access losses (e.g. T&D losses on concerned states and ISTS losses, if applicable)
Key Takeaways
Since the applicable open access losses are different in Chhattisgarh and Madhya Pradesh, the required captive solar capacities at generation-end also vary based on the different location-options
However, for Non-Captive portion (i.e., for surplus sale), capacity of the plant will be as estimated in the previous slide, and it can be located anywhere in CG or MP subject to availability of suitable land
Total Capacity: 306 MW
Total Capacity: 332 MW
Total Capacity: 295 MW

## Slide 23: Financial Assessment of various Business Models for Self-Consumption

## Slide 24
PROJECTION OF DISCOM ENERGY CHARGES AND OPEN ACCESS CHARGES

## Slide 25: Projections of Discom Energy Charge Rates
Energy Charge Rate for Various Categories in CG and MP
State | Category | Voltage | Load | Unit | FY22 | FY50
CG | HV2 | 33 kV | Flat | Paise/kVAh | 700 | 1422
CG | HV2 | 132 kV | Flat | Paise/kVAh | 675 | 1371
CG | HV3 | 33 kV | Load >15% | Paise/kVAh | 670 | 1361
CG | HV3 | 33 kV | Load <15% | Paise/kVAh | 690 | 1401
CG | HV3 | 11 kV | Load >15% | Paise/kVAh | 710 | 1442
CG | HV3 | 11 kV | Load <15% | Paise/kVAh | 730 | 1483
CG | HV7 | 33 kV | Flat | Paise/kVAh | 820 | 1666
CG | HV7 | 11 kV | Flat | Paise/kVAh | 820 | 1666
CG | EHV2 | 132 kV | Flat | Paise/kVAh | 675 | 1371
MP | HV2 | 33 kV | Load >50% | Paise/kWh | 620 | 1259
MP | HV2 | 33 kV | Load <50% | Paise/kWh | 715 | 1452
MP | HV2.1 | 33 kV | Load >50% | Paise/kWh | 620 | 1259
MP | HV2.1 | 33 kV | Load <50% | Paise/kWh | 715 | 1452
MP | HV3.2 | 33 kV | Load >50% | Paise/kWh | 630 | 1280
MP | HV3.2 | 33 kV | Load <50% | Paise/kWh | 725 | 1473
MP | HV3.2 | 11kV | Load >50% | Paise/kWh | 655 | 1330
MP | HV3.2 | 11kV | Load <50% | Paise/kWh | 745 | 1513
MP | HV6 | 33 kV | Load >50% | Paise/kWh | 540 | 1097
MP | HV6 | 33 kV | Load <50% | Paise/kWh | 610 | 1239
MP | HV6.1 | 33 kV | Load >50% | Paise/kWh | 540 | 1097
MP | HV6.1 | 33 kV | Load <50% | Paise/kWh | 610 | 1239
Since EHV2 category tariff of CG is not found, HV2 rates are considered
Key Takeaways
Energy Charges have been projected based on historical CAGR

## Slide 26: Projections of Other Regulatory Charges related to Open Access (1/2)
Energy Charge, Open Access Charge (STU Charge), SLDC Charge and other charges trajectory till the Project Tenure
STU Charge (Rs./kWh)
Chart: 
| CG (for other state gen/ cons) | MP
FY22 | 0.326 | 0.88
FY50 | 0.653 | 3.45
SLDC Charge
Chart: 
| CG-for other state gen/cons (Rs/Day)* | MP (Rs/MW/Yr)**
FY22 | 2000 | 0
FY50 | 2000 | 0
For intra-state RE projects in CG, the charge is zero and the same has been considered in the model, wherever applicable
For intra-state RE projects in CG, the charge is zero and the same has been taken
* No changes in the charge for last few years, hence taken as same
** The charge is zero for RE projects in MP
Source: Respective State’s SERC Tariff Orders for FY22 and Deloitte Analysis
Key Takeaways
For Intra-state renewable plants in CG (generation and consumption both in CG), the STU charge and SLDC charge is 0 (zero)
For plants which are located in other state, or consumer is in other state, the STU charges in CG are expected to rise to almost 2X than the current level, while STU charge in MP is expected to rise significantly to almost 4X than current level
SLDC charge in CG has not changed in last 6 years, hence the trajectory is taken at a flat level
For Renewable plants in MP, the SLDC charge is waived

## Slide 27: Projections of Other Regulatory Charges related to Open Access (2/2)
Energy Charge, Open Access Charge (STU Charge), SLDC Charge and other charges trajectory till the Project Tenure
Wheeling Charge (Rs./kWh)
Chart: 
| CG (for other state gen/ cons) | MP
FY22 | 0.203 | 0.21
FY50 | 0.242 | 0.246
Additional Surcharges
Chart: 
| CG-for other state gen/cons (Rs/Day)* | MP (Rs/MW/Yr)**
FY22 | 0 | 1.11
FY50 | 0 | 4.35
For intra-state RE projects in CG, the charge is zero and the same has been taken
For CG and MP’s wheeling charge projection, it has been found that the charges are fluctuating in a specific range, hence, the average of recent years has been taken
* No mention of additional surcharge is found in CG regulation
Additional:
For captive power plant in every state, the Cross subsidy surcharges and not applicable, otherwise it is applicable and the same has been considered based on its trajectory
CG’s unique Reactive Energy Charge is estimated to stay same at Rs. 0.27/kVAh, considering the last few years trend
Key Takeaways
For Intra-state renewable plants in CG (generation and consumption both in CG), the wheeling charge is 0 (zero)
There is no provision for additional surcharge found in Chhattisgarh Tariff Orders
MP has a very high additional surcharge which is expected to rise 4X in next 25 years and is a critical factor in landed cost of energy in the state and has no waiver
Source: Respective State’s SERC Tariff Orders for FY22 and Deloitte Analysis

## Slide 28
MODEL 1: CAPTIVE MODE FINANCIAL EVALUATION AND FINDINGS

## Slide 29: Charges Applicable for Various Options- Captive
Regulatory Charges and Losses Applicable for various options in the captive mode
Regulatory Charges & Losses Applicability | Option 1: Entire Capacity is in CG |  | Option 2: Entire Capacity is in MP |  | Option 3: CG-Own, MP-Own | 
 | Energy to CG | Energy to MP | Energy to CG | Energy to MP | Energy to CG | Energy to MP
CG-Transmission Charge |  |  |  |  |  | 
CG-SLDC Charge |  |  |  |  |  | 
CG-Wheeling Charge |  |  |  |  |  | 
CG-Cross Subsidy Surcharge |  |  |  |  |  | 
CG-Additional Surcharge |  |  |  |  |  | 
CG-Reactive Energy Charge |  |  |  |  |  | 
CG-T&D Loss |  |  |  |  |  | 
ISTS Charge |  |  |  |  |  | 
ISTS Loss |  |  |  |  |  | 
MP-Transmission Charge |  |  |  |  |  | 
MP-Wheeling Charge |  |  |  |  |  | 
MP-SLDC Charge |  |  |  |  |  | 
MP-Cross Subsidy Surcharge |  |  |  |  |  | 
MP-Additional Surcharge |  |  |  |  |  | 
MP-T&D Loss |  |  |  |  |  | 
Key Takeaways
ISTS charge (if not waived) and ISTS loss, will be applicable for Option 1 and 2, but not for Option 3, I,e, respective states having their own generation requirement. This may lead to a huge savings if the charge is not waived off. Clarification needs to be obtained from MoP regarding applicability of the MoP order dated 23.11.2021 on ISTS charge waiver.

## Slide 30
MODEL 1a: CAPTIVE SOLAR PLANT ON OWN LAND

## Slide 31: Option 1: Comparison of Cost of Energy- Own Land (Rs./KWh)
For Option 1: Full Generation in CG and Consumption in both
@Rs. 6.35 Cr/MW Capex
@Rs. 5.72 Cr/ MW Capex
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost | 3.74 | 3.72 | 3.7 | 3.65 | 3.61 | 3.56 | 3.52 | 3.46 | 3.42 | 3.38 | 3.33 | 3.27 | 3.24 | 3.19 | 3.14 | 1.63 | 1.06 | 1 | 0.94 | 0.88 | 0.82 | 0.81 | 0.85 | 0.88 | 0.92 | 0.96
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost- without ISTS waiver | 11.9 | 12.15 | 12.4 | 12.63 | 12.89 | 13.15 | 13.42 | 13.69 | 14 | 14.32 | 14.65 | 14.98 | 15.35 | 15.73 | 16.13 | 14.83 | 14.64 | 15.08 | 15.54 | 16.02 | 16.54 | 17.13 | 17.8 | 18.49 | 19.22 | 19.98
MP-Solar Generation Cost- with ISTS waiver | 7.95 | 8.06 | 8.19 | 8.27 | 8.39 | 8.5 | 8.62 | 8.74 | 8.89 | 9.03 | 9.19 | 9.34 | 9.53 | 9.72 | 9.92 | 8.41 | 8.02 | 8.24 | 8.48 | 8.73 | 9 | 9.34 | 9.76 | 10.19 | 10.65 | 11.12
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost | 4.12 | 4.1 | 4.08 | 4.01 | 3.97 | 3.92 | 3.86 | 3.8 | 3.76 | 3.7 | 3.65 | 3.58 | 3.54 | 3.49 | 3.43 | 1.75 | 1.11 | 1.04 | 0.97 | 0.9 | 0.83 | 0.82 | 0.85 | 0.89 | 0.93 | 0.97
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost- without ISTS waiver | 12.35 | 12.59 | 12.84 | 13.06 | 13.31 | 13.56 | 13.83 | 14.09 | 14.4 | 14.7 | 15.02 | 15.35 | 15.71 | 16.08 | 16.47 | 14.97 | 14.7 | 15.13 | 15.58 | 16.05 | 16.55 | 17.13 | 17.81 | 18.5 | 19.23 | 19.99
MP-Solar Generation Cost- with ISTS waiver | 8.4 | 8.51 | 8.63 | 8.7 | 8.81 | 8.92 | 9.03 | 9.14 | 9.28 | 9.42 | 9.56 | 9.71 | 9.89 | 10.07 | 10.26 | 8.55 | 8.08 | 8.29 | 8.52 | 8.75 | 9.02 | 9.35 | 9.77 | 10.2 | 10.66 | 11.13
Key Takeaways
Projected ECR for CG is always expected to be higher than CG- solar landed cost, while in MP if ISTS charge is not waived the cost is far higher than projected ECR and if it is waived then also most of the time ECR is lower than solar landed cost’
Source: Deloitte Analysis

## Slide 32: Option 2: Comparison of Cost of Energy- Own Land (Rs./KWh)
For Option 2: Full Capacity in MP and consumption in both
@Rs. 6.35 Cr/MW Capex
@rs. 5.72 Cr/ MW Capex
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost-without ISTS Waiver | 10.99 | 11.17 | 11.35 | 11.49 | 11.67 | 11.84 | 12.02 | 12.2 | 12.41 | 12.62 | 12.84 | 13.06 | 13.31 | 13.57 | 13.83 | 12.2 | 11.8 | 12.09 | 12.39 | 12.71 | 13.04 | 13.45 | 13.95 | 14.45 | 14.99 | 15.53
CG-Solar Generation Cost-with ISTS Waiver | 7.05 | 7.1 | 7.15 | 7.16 | 7.19 | 7.22 | 7.25 | 7.27 | 7.32 | 7.36 | 7.41 | 7.45 | 7.52 | 7.58 | 7.65 | 5.82 | 5.21 | 5.28 | 5.36 | 5.45 | 5.54 | 5.71 | 5.95 | 6.19 | 6.45 | 6.72
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost-without ISTS Waiver | 10.54 | 10.72 | 10.91 | 11.06 | 11.24 | 11.42 | 11.61 | 11.8 | 12.02 | 12.24 | 12.47 | 12.69 | 12.95 | 13.22 | 13.49 | 12.06 | 11.74 | 12.04 | 12.35 | 12.68 | 13.03 | 13.45 | 13.94 | 14.44 | 14.98 | 15.52
CG-Solar Generation Cost-with ISTS Waiver | 6.61 | 6.66 | 6.71 | 6.73 | 6.77 | 6.8 | 6.84 | 6.87 | 6.93 | 6.98 | 7.03 | 7.08 | 7.16 | 7.23 | 7.31 | 5.68 | 5.15 | 5.23 | 5.32 | 5.42 | 5.53 | 5.7 | 5.94 | 6.18 | 6.45 | 6.71
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost | 6.96 | 7.07 | 7.18 | 7.25 | 7.36 | 7.45 | 7.56 | 7.67 | 7.8 | 7.93 | 8.07 | 8.21 | 8.38 | 8.55 | 8.74 | 7.25 | 6.85 | 7.05 | 7.27 | 7.5 | 7.75 | 8.07 | 8.47 | 8.87 | 9.31 | 9.76
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost | 6.57 | 6.68 | 6.79 | 6.87 | 6.98 | 7.09 | 7.2 | 7.31 | 7.45 | 7.59 | 7.74 | 7.89 | 8.07 | 8.25 | 8.44 | 7.12 | 6.79 | 7.01 | 7.24 | 7.48 | 7.74 | 8.07 | 8.46 | 8.86 | 9.3 | 9.75
Key Takeaways
For CG, ISTS charge waiver plays a critical role in the cost comparison. If it is waived, solar landed cost is always lower than projected ECR, but if it is not waived, the costs come closer
For MP, overall solar generation landed cost is marginally less (though going above sometimes) than the projected ECR
Source: Deloitte Analysis

## Slide 33: Option 3: Comparison of Cost of Energy- Own Land (Rs./KWh)
For Option 3: CG demand met by CG capacity, MP demand met by capacities in MP
@Rs. 6.35 Cr/MW Capex
@Rs. 5.72 Cr/ MW Capex
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost | 6.96 | 7.07 | 7.18 | 7.25 | 7.36 | 7.45 | 7.56 | 7.67 | 7.8 | 7.93 | 8.07 | 8.21 | 8.38 | 8.55 | 8.74 | 7.25 | 6.85 | 7.05 | 7.27 | 7.5 | 7.75 | 8.07 | 8.47 | 8.87 | 9.31 | 9.76
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost | 6.57 | 6.68 | 6.79 | 6.87 | 6.98 | 7.09 | 7.2 | 7.31 | 7.45 | 7.59 | 7.74 | 7.89 | 8.07 | 8.25 | 8.44 | 7.12 | 6.79 | 7.01 | 7.24 | 7.48 | 7.74 | 8.07 | 8.46 | 8.86 | 9.3 | 9.75
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost | 4.12 | 4.1 | 4.08 | 4.01 | 3.97 | 3.92 | 3.86 | 3.8 | 3.76 | 3.7 | 3.65 | 3.58 | 3.54 | 3.49 | 3.43 | 1.75 | 1.11 | 1.04 | 0.97 | 0.9 | 0.83 | 0.82 | 0.85 | 0.89 | 0.93 | 0.97
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost | 3.74 | 3.72 | 3.7 | 3.65 | 3.61 | 3.56 | 3.52 | 3.46 | 3.42 | 3.38 | 3.33 | 3.27 | 3.24 | 3.19 | 3.14 | 1.63 | 1.06 | 1 | 0.94 | 0.88 | 0.82 | 0.81 | 0.85 | 0.88 | 0.92 | 0.96
Key Takeaways
For CG, the solar landed cost per unit is always less than projected ECR, leading to a savings
For MP, overall solar generation landed cost is marginally less (though going above sometimes) than the projected ECR
Source: Deloitte Analysis

## Slide 34: Savings (Rs. Crore)- For Own Land
 |  | Option 1: Entire Capacity is in CG |  |  | Option 2: Entire Capacity is in MP |  | Option 2: Entire Capacity is in MP | Option 3: CG-Own, MP-Own | Option 3: CG-Own, MP-Own
Total Savings (Rs. Crore.) for Entire Project Tenure for Multiple Capex Scenario |  | CG Savings | MP Savings | MP Savings- If ISTS Charge Waived off | CG Savings | CG Savings- If ISTS Charge Waived off | MP Savings | CG Savings | MP Savings
At D:E 80:20 | Base Case Capex | 9662.17 | -2144.03 | 305.48 | -795.10 | 5466.30 | 880.27 | 9662.17 | 880.27
 | 10% Discounted Capex | 9894.11 | -2038.00 | 411.51 | -522.67 | 5738.73 | 973.81 | 9894.11 | 973.81
At D:E 50:50 | Base Case Capex | 10036.45 | -1972.92 | 476.59 | -355.47 | 5905.93 | 1031.21 | 10036.45 | 1031.21
 | 10% Discounted Capex | 10230.95 | -1884.00 | 565.51 | -127.00 | 6134.40 | 1109.66 | 10230.95 | 1109.66
At D:E 0:100 | Base Case Capex | 10624.48 | -1704.09 | 745.42 | 335.25 | 6596.65 | 1268.37 | 10624.48 | 1268.37
 | 10% Discounted Capex | 10760.18 | -1642.05 | 807.46 | 494.64 | 6756.04 | 1323.10 | 10760.18 | 1323.10
For various Options
Base case Capex: Rs. 6.35 Cr/MW
10% discounted Capex: Rs. 5.72 Cr/ Mw
Key Takeaways
Option 3 has highest savings, followed by Option 1 with ISTS charge waiver and ISTS charge non-waived case
Option 2 has the least savings
Source: Deloitte Analysis

## Slide 35: Equity IRR (%)- Own Land
For various Options
Base case Capex: Rs. 6.35 Cr/MW
10% discounted Capex: Rs. 5.72 Cr/ Mw
Key Takeaways
Option 3 has highest equity IRR, followed by Option 1 with ISTS charge waiver and ISTS charge non-waived case
Option 2 has the lowest Equity IRR options for various Capex and Debt-Equity scenario
80:20 Debt: Equity Ratio has highest achievable Equity IRR
Source: Deloitte Analysis
Equity IRR (%) |  | Option 1: Entire Capacity is in CG |  | Option 2: Entire Capacity is in MP |  | Option 3: CG-Own, MP-Own
 |  | ISTS Applicable | ISTS Waived | ISTS Applicable | ISTS Waived | 
At D:E 80:20 | Base Case Capex | 32% | 44% | -1% | 24% | 50%
 | 10% Discounted Capex | 39% | 53% | 0% | 30% | 59%
At D:E 50:50 | Base Case Capex | 18% | 24% | -1% | 15% | 27%
 | 10% Discounted Capex | 22% | 28% | 0% | 17% | 31%
At D:E 0:100 | Base Case Capex | 13% | 16% | -1% | 10% | 18%
 | 10% Discounted Capex | 15% | 18% | 0% | 12% | 20%

## Slide 36
MODEL 1b: CAPTIVE SOLAR PLANT ON OTHER’S LAND

## Slide 37: Option 1: Comparison of Cost of Energy- Others’ Land (Rs./KWh)
For Option 1: Full Generation in CG and Consumption in both
@Rs. 6.75 Cr/MW Capex
@Rs. 6.12 Cr/ MW Capex
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost | 4.26 | 4.23 | 4.21 | 4.14 | 4.09 | 4.03 | 3.97 | 3.9 | 3.86 | 3.8 | 3.74 | 3.67 | 3.62 | 3.55 | 3.49 | 1.79 | 1.14 | 1.07 | 0.99 | 0.91 | 0.84 | 0.82 | 0.85 | 0.89 | 0.93 | 0.97
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost- without ISTS waiver | 12.51 | 12.75 | 13 | 13.2 | 13.45 | 13.7 | 13.96 | 14.21 | 14.51 | 14.81 | 15.12 | 15.44 | 15.8 | 16.16 | 16.54 | 15.02 | 14.74 | 15.16 | 15.6 | 16.07 | 16.56 | 17.14 | 17.81 | 18.5 | 19.24 | 19.99
MP-Solar Generation Cost- with ISTS waiver | 8.56 | 8.67 | 8.78 | 8.85 | 8.95 | 9.05 | 9.16 | 9.26 | 9.39 | 9.52 | 9.66 | 9.8 | 9.98 | 10.15 | 10.33 | 8.6 | 8.11 | 8.32 | 8.54 | 8.77 | 9.02 | 9.35 | 9.77 | 10.2 | 10.66 | 11.13
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost | 3.88 | 3.86 | 3.83 | 3.77 | 3.73 | 3.68 | 3.63 | 3.56 | 3.52 | 3.47 | 3.42 | 3.35 | 3.31 | 3.26 | 3.2 | 1.68 | 1.09 | 1.02 | 0.96 | 0.89 | 0.83 | 0.81 | 0.85 | 0.88 | 0.93 | 0.96
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost- without ISTS waiver | 12.06 | 12.31 | 12.56 | 12.77 | 13.03 | 13.28 | 13.55 | 13.81 | 14.12 | 14.43 | 14.75 | 15.07 | 15.44 | 15.81 | 16.2 | 14.88 | 14.68 | 15.11 | 15.57 | 16.04 | 16.54 | 17.13 | 17.8 | 18.49 | 19.23 | 19.98
MP-Solar Generation Cost- with ISTS waiver | 8.11 | 8.22 | 8.34 | 8.42 | 8.53 | 8.63 | 8.75 | 8.86 | 9 | 9.14 | 9.29 | 9.44 | 9.62 | 9.8 | 9.99 | 8.46 | 8.05 | 8.27 | 8.5 | 8.74 | 9.01 | 9.34 | 9.76 | 10.19 | 10.65 | 11.12
Key Takeaways
Projected ECR for CG is always expected to be higher than CG- solar landed cost, while in MP if ISTS charge is not waived the cost is far higher than projected ECR and if it is waived then also most of the time ECR is lower than solar landed cost’
Source: Deloitte Analysis

## Slide 38: Option 2: Comparison of Cost of Energy- Others’ Land (Rs./KWh)
For Option 2: Full Capacity in MP and consumption in both
@Rs. 6.83 Cr/MW Capex
@Rs. 6.20 Cr/ MW Capex
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost-without ISTS Waiver | 11.18 | 11.35 | 11.53 | 11.67 | 11.84 | 12 | 12.18 | 12.35 | 12.55 | 12.75 | 12.96 | 13.17 | 13.42 | 13.66 | 13.92 | 12.26 | 11.85 | 12.13 | 12.42 | 12.72 | 13.05 | 13.46 | 13.95 | 14.45 | 14.99 | 15.53
CG-Solar Generation Cost-with ISTS Waiver | 7.25 | 7.29 | 7.33 | 7.33 | 7.36 | 7.38 | 7.4 | 7.42 | 7.46 | 7.49 | 7.53 | 7.56 | 7.62 | 7.68 | 7.74 | 5.88 | 5.26 | 5.32 | 5.39 | 5.46 | 5.55 | 5.71 | 5.95 | 6.19 | 6.46 | 6.72
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost | 7.13 | 7.23 | 7.34 | 7.41 | 7.5 | 7.6 | 7.7 | 7.79 | 7.92 | 8.05 | 8.18 | 8.31 | 8.48 | 8.64 | 8.82 | 7.3 | 6.89 | 7.08 | 7.29 | 7.52 | 7.76 | 8.08 | 8.47 | 8.88 | 9.31 | 9.76
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost | 6.74 | 6.84 | 6.95 | 7.03 | 7.13 | 7.23 | 7.34 | 7.44 | 7.57 | 7.71 | 7.85 | 7.99 | 8.16 | 8.33 | 8.52 | 7.18 | 6.83 | 7.04 | 7.26 | 7.49 | 7.75 | 8.07 | 8.46 | 8.87 | 9.3 | 9.75
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost-without ISTS Waiver | 10.73 | 10.91 | 11.09 | 11.24 | 11.41 | 11.59 | 11.77 | 11.95 | 12.16 | 12.37 | 12.59 | 12.81 | 13.06 | 13.31 | 13.58 | 12.12 | 11.79 | 12.08 | 12.38 | 12.7 | 13.04 | 13.45 | 13.94 | 14.44 | 14.98 | 15.52
CG-Solar Generation Cost-with ISTS Waiver | 6.8 | 6.85 | 6.89 | 6.9 | 6.94 | 6.96 | 6.99 | 7.02 | 7.07 | 7.11 | 7.16 | 7.2 | 7.27 | 7.33 | 7.4 | 5.74 | 5.19 | 5.27 | 5.35 | 5.44 | 5.54 | 5.7 | 5.94 | 6.18 | 6.45 | 6.71
Source: Deloitte Analysis
Key Takeaways
For CG, ISTS charge waiver plays a critical role in the cost comparison. If it is waived, solar landed cost is always lower than projected ECR, but if it is not waived, the costs come closer
For MP, overall solar generation landed cost is marginally less (though going above sometimes) than the projected ECR

## Slide 39: Option 3: Comparison of Cost of Energy- Others’ Land (Rs./KWh)
For Option 3: CG demand met by CG capacity, MP demand met by capacities in MP
@Rs. 6.78 Cr/MW Capex
@Rs. 6.14 Cr/ MW Capex
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost | 7.11 | 7.21 | 7.32 | 7.39 | 7.49 | 7.58 | 7.68 | 7.78 | 7.91 | 8.03 | 8.17 | 8.3 | 8.46 | 8.63 | 8.81 | 7.3 | 6.88 | 7.08 | 7.29 | 7.51 | 7.76 | 8.08 | 8.47 | 8.88 | 9.31 | 9.76
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost | 6.72 | 6.82 | 6.93 | 7.01 | 7.11 | 7.21 | 7.32 | 7.43 | 7.56 | 7.69 | 7.83 | 7.98 | 8.15 | 8.32 | 8.51 | 7.17 | 6.83 | 7.04 | 7.26 | 7.49 | 7.75 | 8.07 | 8.46 | 8.87 | 9.3 | 9.75
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost | 4.26 | 4.24 | 4.21 | 4.14 | 4.1 | 4.04 | 3.98 | 3.91 | 3.86 | 3.8 | 3.74 | 3.67 | 3.62 | 3.56 | 3.5 | 1.8 | 1.14 | 1.07 | 0.99 | 0.91 | 0.84 | 0.82 | 0.85 | 0.89 | 0.93 | 0.97
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost | 3.88 | 3.86 | 3.84 | 3.78 | 3.74 | 3.68 | 3.63 | 3.57 | 3.53 | 3.47 | 3.42 | 3.36 | 3.31 | 3.26 | 3.21 | 1.68 | 1.09 | 1.02 | 0.96 | 0.89 | 0.83 | 0.81 | 0.85 | 0.88 | 0.93 | 0.96
Source: Deloitte Analysis
Key Takeaways
For CG, the solar landed cost per unit is always less than projected ECR, leading to a savings
For MP, overall solar generation landed cost is marginally less (though going above sometimes) than the projected ECR

## Slide 40: Savings (Rs. Crore)- For Others’ Land
 |  | Option 1: Entire Capacity is in CG |  |  | Option 2: Entire Capacity is in MP |  | Option 2: Entire Capacity is in MP | Option 3: CG-Own, MP-Own | Option 3: CG-Own, MP-Own
Total Savings (Rs. Crore.) for Entire Project Tenure for Multiple Capex Scenario |  | CG Savings | MP Savings | MP Savings- If ISTS Charge Waived off | CG Savings | CG Savings- If ISTS Charge Waived off | MP Savings | CG Savings | MP Savings
At D:E 80:20 | Base Case Capex | 9590.29 | -2176.89 | 272.61 | -896.30 | 5365.10 | 845.52 | 9586.19 | 849.62
 | 10% Discounted Capex | 9822.27 | -2070.84 | 378.67 | -623.81 | 5637.59 | 939.08 | 9818.17 | 943.18
At D:E 50:50 | Base Case Capex | 9991.00 | -1993.70 | 455.81 | -419.35 | 5842.05 | 1009.28 | 9988.43 | 1011.85
 | 10% Discounted Capex | 10185.58 | -1904.74 | 544.77 | -190.79 | 6070.61 | 1087.76 | 10183.01 | 1090.33
At D:E 0:100 | Base Case Capex | 10620.54 | -1705.89 | 743.62 | 329.69 | 6591.09 | 1266.46 | 10620.31 | 1266.69
 | 10% Discounted Capex | 10756.24 | -1643.85 | 805.66 | 489.08 | 6750.48 | 1321.19 | 10756.01 | 1321.42
For various Options
Chhattisgarh-Full
Base case Capex: Rs. 6.75 Cr/MW
10% discounted Capex: Rs. 6.12 Cr/ Mw
MP-Full
Base case Capex: Rs. 6.83 Cr/MW
10% discounted Capex: Rs.6.20 Cr/ Mw
CG-Self & MP-Self
Base case Capex: Rs. 6.78 Cr/MW
10% discounted Capex: Rs.6.14 Cr/ Mw
Source: Deloitte Analysis
Key Takeaways
Option 3 has highest savings, followed by Option 1 with ISTS charge waiver and ISTS charge non-waived case
Option 2 has the least savings

## Slide 41: Equity IRR (%)- Others’ Land
For various Options
Chhattisgarh-Full
Base case Capex: Rs. 6.75 Cr/MW
10% discounted Capex: Rs. 6.12 Cr/ Mw
MP-Full
Base case Capex: Rs. 6.83 Cr/MW
10% discounted Capex: Rs.6.20 Cr/ Mw
CG-Self & MP-Self
Base case Capex: Rs. 6.78 Cr/MW
10% discounted Capex: Rs.6.14 Cr/ Mw
Key Takeaways
Option 3 has highest equity IRR, followed by Option 1 with ISTS charge waiver and ISTS charge non-waived case
Option 2 has the lowest Equity IRR options for various Capex and Debt-Equity scenario
80:20 Debt: Equity Ratio has highest achievable Equity IRR
Source: Deloitte Analysis
Equity IRR (%) |  | Option 1: Entire Capacity is in CG |  | Option 2: Entire Capacity is in MP |  | Option 3: CG-Own, MP-Own
 |  | ISTS Applicable | ISTS Waived | ISTS Applicable | ISTS Waived | 
At D:E 80:20 | Base Case Capex | 29% | 40% | -1% | 21% | 45%
 | 10% Discounted Capex | 35% | 48% | 0% | 27% | 53%
At D:E 50:50 | Base Case Capex | 17% | 22% | -2% | 13% | 24%
 | 10% Discounted Capex | 20% | 26% | -1% | 16% | 28%
At D:E 0:100 | Base Case Capex | 12% | 15% | -2% | 9% | 16%
 | 10% Discounted Capex | 14% | 17% | -1% | 11% | 18%

## Slide 42
MODEL 2: BOO (PPA-BASED) FINANCIAL EVALUATION AND FINDINGS

## Slide 43: Charges Applicable for Various Options- BOO
Regulatory Charges and Losses Applicable
Regulatory Charges & Losses Applicability | Option 1: Entire Capacity is in CG |  | Option 2: Entire Capacity is in MP |  | Option 3: CG-Own, MP-Own | 
 | Energy to CG | Energy to MP | Energy to CG | Energy to MP | Energy to CG | Energy to MP
CG-Transmission Charge |  |  |  |  |  | 
CG-SLDC Charge |  |  |  |  |  | 
CG-Wheeling Charge |  |  |  |  |  | 
CG-Cross Subsidy Surcharge |  |  |  |  |  | 
CG-Additional Surcharge |  |  |  |  |  | 
CG-Reactive Energy Charge |  |  |  |  |  | 
CG-T&D Loss |  |  |  |  |  | 
ISTS Charge |  |  |  |  |  | 
ISTS Loss |  |  |  |  |  | 
MP-Transmission Charge |  |  |  |  |  | 
MP-Wheeling Charge |  |  |  |  |  | 
MP-SLDC Charge |  |  |  |  |  | 
MP-Cross Subsidy Surcharge |  |  |  |  |  | 
MP-Additional Surcharge |  |  |  |  |  | 
MP-T&D Loss |  |  |  |  |  | 
Key Takeaways
ISTS charge and loss will not at all be applicable for Option 3
CG doesn’t have additional surcharge in their regulations, hence not applicable
CG has waiver for insta-state RE on STU charge, wheeling charges, SLDC charges, while MP only has SLDC charge waived for RE plants

## Slide 44: Option 1: Comparison of Cost of Energy- BOO (Rs./KWh)
For Option 1: Full Generation in CG and Consumption in both
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost @Rs. 2.20/kwh tariff | 2.45 | 2.44 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45
CG-Solar Generation Cost @Rs. 2.50/kwh tariff | 2.77 | 2.75 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77
CG-Solar Generation Cost @Rs. 3.00/kwh tariff | 3.3 | 3.28 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
CG-Solar Generation Cost @Rs. 3.50/kwh tariff | 3.84 | 3.81 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84
CG-Solar Generation Cost @Rs. 4.00/kwh tariff | 4.37 | 4.34 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost @Rs. 2.20/kwh- without ISTS waiver | 12.15 | 12.39 | 12.69 | 12.98 | 13.28 | 13.6 | 13.92 | 14.26 | 14.62 | 14.99 | 15.37 | 15.77 | 16.19 | 16.62 | 17.07 | 17.54 | 18.03 | 18.54 | 19.08 | 19.63 | 20.21 | 20.81 | 21.44 | 22.09 | 22.77 | 23.49
MP-Solar Generation Cost- @ Rs. 2.20/kwh-with ISTS waiver | 8.2 | 8.31 | 8.47 | 8.63 | 8.79 | 8.95 | 9.12 | 9.31 | 9.5 | 9.7 | 9.91 | 10.13 | 10.36 | 10.61 | 10.86 | 11.13 | 11.41 | 11.7 | 12.01 | 12.33 | 12.67 | 13.03 | 13.4 | 13.79 | 14.2 | 14.63
MP-Solar Generation Cost- @Rs. 2.50/kwh without ISTS waiver | 12.5291 | 12.764 | 13.061 | 13.3574 | 13.6586 | 13.9706 | 14.2976 | 14.6389 | 14.9928 | 15.3614 | 15.7456 | 16.1457 | 16.5621 | 16.9959 | 17.4478 | 17.9184 | 18.4087 | 18.9195 | 19.4517 | 20.0062 | 20.584 | 21.1861 | 21.8137 | 22.4677 | 23.1495 | 23.8601
MP-Solar Generation Cost- @Rs. 2.50/kwh with ISTS waiver | 8.5753 | 8.6806 | 8.8438 | 9.0019 | 9.1602 | 9.3247 | 9.4994 | 9.6834 | 9.8749 | 10.0756 | 10.2865 | 10.5076 | 10.7392 | 10.9821 | 11.2368 | 11.5038 | 11.7837 | 12.0773 | 12.3852 | 12.708 | 13.0465 | 13.4015 | 13.7738 | 14.1643 | 14.5738 | 15.0033
MP-Solar Generation Cost- @Rs. 3.00/kwh without ISTS waiver | 13.1539 | 13.3844 | 13.6858 | 13.9822 | 14.2834 | 14.5954 | 14.9224 | 15.2637 | 15.6176 | 15.9862 | 16.3704 | 16.7705 | 17.1869 | 17.6207 | 18.0726 | 18.5432 | 19.0335 | 19.5443 | 20.0765 | 20.631 | 21.2088 | 21.8109 | 22.4385 | 23.0925 | 23.7743 | 24.4849
MP-Solar Generation Cost- @Rs. 3.00/kwh with ISTS waiver | 9.2001 | 9.301 | 9.4686 | 9.6267 | 9.785 | 9.9495 | 10.1242 | 10.3082 | 10.4997 | 10.7004 | 10.9113 | 11.1324 | 11.364 | 11.6069 | 11.8616 | 12.1286 | 12.4085 | 12.7021 | 13.01 | 13.3328 | 13.6713 | 14.0263 | 14.3986 | 14.7891 | 15.1986 | 15.6281
MP-Solar Generation Cost- @Rs. 3.50/kwh without ISTS waiver | 13.7787 | 14.0048 | 14.3106 | 14.607 | 14.9082 | 15.2202 | 15.5472 | 15.8885 | 16.2424 | 16.611 | 16.9952 | 17.3953 | 17.8117 | 18.2455 | 18.6974 | 19.168 | 19.6583 | 20.1691 | 20.7013 | 21.2558 | 21.8336 | 22.4357 | 23.0633 | 23.7173 | 24.3991 | 25.1097
MP-Solar Generation Cost- @Rs. 3.50/kwh with ISTS waiver | 9.8249 | 9.9214 | 10.0934 | 10.2515 | 10.4098 | 10.5743 | 10.749 | 10.933 | 11.1245 | 11.3252 | 11.5361 | 11.7572 | 11.9888 | 12.2317 | 12.4864 | 12.7534 | 13.0333 | 13.3269 | 13.6348 | 13.9576 | 14.2961 | 14.6511 | 15.0234 | 15.4139 | 15.8234 | 16.2529
MP-Solar Generation Cost- @Rs. 4.00/kwh without ISTS waiver | 14.4035 | 14.6252 | 14.9354 | 15.2318 | 15.533 | 15.845 | 16.172 | 16.5133 | 16.8672 | 17.2358 | 17.62 | 18.0201 | 18.4365 | 18.8703 | 19.3222 | 19.7928 | 20.2831 | 20.7939 | 21.3261 | 21.8806 | 22.4584 | 23.0605 | 23.6881 | 24.3421 | 25.0239 | 25.7345
MP-Solar Generation Cost- @Rs. 4.00/kwh with ISTS waiver | 10.4497 | 10.5418 | 10.7181 | 10.8763 | 11.0346 | 11.1991 | 11.3738 | 11.5578 | 11.7493 | 11.95 | 12.1609 | 12.382 | 12.6136 | 12.8565 | 13.1112 | 13.3782 | 13.6581 | 13.9517 | 14.2596 | 14.5824 | 14.9209 | 15.2759 | 15.6482 | 16.0387 | 16.4482 | 16.8777
Key Takeaways
Landed solar cost at CG is always lower than projected ECR, while for MP, the cost is always higher, irrespective of the applicability of ISTS charges

## Slide 45: Option 2: Comparison of Cost of Energy- BOO (Rs./KWh)
For Option 2: Full Capacity in MP and consumption in both
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost @Rs. 2.20/kwh tariff | 7 | 7.1 | 7.24 | 7.39 | 7.54 | 7.69 | 7.85 | 8.02 | 8.2 | 8.39 | 8.59 | 8.79 | 9.01 | 9.24 | 9.48 | 9.73 | 9.99 | 10.27 | 10.56 | 10.87 | 11.19 | 11.52 | 11.88 | 12.25 | 12.64 | 13.05
MP-Solar Generation Cost @Rs. 2.50/kwh tariff | 7.33 | 7.43 | 7.58 | 7.72 | 7.87 | 8.02 | 8.18 | 8.35 | 8.53 | 8.72 | 8.92 | 9.12 | 9.34 | 9.57 | 9.81 | 10.06 | 10.32 | 10.6 | 10.89 | 11.2 | 11.52 | 11.85 | 12.21 | 12.58 | 12.97 | 13.38
MP-Solar Generation Cost @Rs. 3.00/kwh tariff | 7.88 | 7.97 | 8.13 | 8.27 | 8.42 | 8.57 | 8.73 | 8.9 | 9.08 | 9.27 | 9.47 | 9.67 | 9.89 | 10.12 | 10.36 | 10.61 | 10.87 | 11.15 | 11.44 | 11.75 | 12.07 | 12.41 | 12.76 | 13.13 | 13.52 | 13.93
MP-Solar Generation Cost @Rs. 3.50/kwh tariff | 8.43 | 8.52 | 8.68 | 8.82 | 8.97 | 9.12 | 9.28 | 9.46 | 9.63 | 9.82 | 10.02 | 10.23 | 10.44 | 10.67 | 10.91 | 11.16 | 11.43 | 11.7 | 11.99 | 12.3 | 12.62 | 12.96 | 13.31 | 13.68 | 14.07 | 14.48
MP-Solar Generation Cost @Rs. 4.00/kwh tariff | 8.98 | 9.07 | 9.23 | 9.38 | 9.52 | 9.67 | 9.84 | 10.01 | 10.19 | 10.37 | 10.57 | 10.78 | 10.99 | 11.22 | 11.46 | 11.71 | 11.98 | 12.25 | 12.55 | 12.85 | 13.17 | 13.51 | 13.86 | 14.23 | 14.62 | 15.03
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost @Rs. 2.20/kwh- without ISTS waiver | 10.35 | 10.5 | 10.67 | 10.87 | 11.18 | 11.4 | 11.63 | 11.88 | 12.14 | 12.41 | 12.71 | 13 | 13.3 | 13.62 | 13.95 | 14.29 | 14.65 | 15.01 | 15.4 | 15.8 | 16.21 | 16.64 | 17.09 | 17.55 | 18.04 | 18.54
CG-Solar Generation Cost- @ Rs. 2.20/kwh-with ISTS waiver | 6.42 | 6.43 | 6.47 | 6.54 | 6.7 | 6.78 | 6.86 | 6.95 | 7.04 | 7.16 | 7.27 | 7.39 | 7.51 | 7.63 | 7.77 | 7.91 | 8.05 | 8.21 | 8.37 | 8.54 | 8.71 | 8.9 | 9.09 | 9.29 | 9.51 | 9.73
CG-Solar Generation Cost- @Rs. 2.50/kwh without ISTS waiver | 10.73 | 10.87 | 11.04 | 11.25 | 11.55 | 11.78 | 12.01 | 12.25 | 12.51 | 12.79 | 13.08 | 13.37 | 13.67 | 13.99 | 14.32 | 14.66 | 15.02 | 15.39 | 15.77 | 16.17 | 16.59 | 17.02 | 17.46 | 17.93 | 18.41 | 18.92
CG-Solar Generation Cost- @Rs. 2.50/kwh with ISTS waiver | 6.79 | 6.81 | 6.85 | 6.91 | 7.08 | 7.15 | 7.23 | 7.32 | 7.42 | 7.53 | 7.65 | 7.76 | 7.88 | 8.01 | 8.14 | 8.28 | 8.43 | 8.58 | 8.74 | 8.91 | 9.09 | 9.27 | 9.47 | 9.67 | 9.88 | 10.1
CG-Solar Generation Cost- @Rs. 3.00/kwh without ISTS waiver | 11.35 | 11.49 | 11.67 | 11.87 | 12.18 | 12.4 | 12.63 | 12.88 | 13.14 | 13.41 | 13.71 | 14 | 14.3 | 14.62 | 14.95 | 15.29 | 15.65 | 16.01 | 16.4 | 16.8 | 17.21 | 17.64 | 18.09 | 18.55 | 19.04 | 19.54
CG-Solar Generation Cost- @Rs. 3.00/kwh with ISTS waiver | 7.42 | 7.43 | 7.47 | 7.54 | 7.7 | 7.78 | 7.86 | 7.95 | 8.04 | 8.16 | 8.27 | 8.39 | 8.51 | 8.63 | 8.77 | 8.91 | 9.05 | 9.21 | 9.37 | 9.54 | 9.71 | 9.9 | 10.09 | 10.29 | 10.51 | 10.73
CG-Solar Generation Cost- @Rs. 3.50/kwh without ISTS waiver | 11.97 | 12.11 | 12.29 | 12.5 | 12.8 | 13.03 | 13.26 | 13.5 | 13.76 | 14.04 | 14.33 | 14.62 | 14.92 | 15.24 | 15.57 | 15.91 | 16.27 | 16.64 | 17.02 | 17.42 | 17.84 | 18.27 | 18.71 | 19.18 | 19.66 | 20.16
CG-Solar Generation Cost- @Rs. 3.50/kwh with ISTS waiver | 8.04 | 8.05 | 8.1 | 8.16 | 8.32 | 8.4 | 8.48 | 8.57 | 8.67 | 8.78 | 8.9 | 9.01 | 9.13 | 9.26 | 9.39 | 9.53 | 9.68 | 9.83 | 9.99 | 10.16 | 10.34 | 10.52 | 10.72 | 10.92 | 11.13 | 11.35
CG-Solar Generation Cost- @Rs. 4.00/kwh without ISTS waiver | 12.6 | 12.73 | 12.92 | 13.12 | 13.43 | 13.65 | 13.88 | 14.13 | 14.39 | 14.66 | 14.96 | 15.25 | 15.55 | 15.87 | 16.2 | 16.54 | 16.89 | 17.26 | 17.65 | 18.05 | 18.46 | 18.89 | 19.34 | 19.8 | 20.29 | 20.79
CG-Solar Generation Cost- @Rs. 4.00/kwh with ISTS waiver | 8.67 | 8.67 | 8.72 | 8.79 | 8.95 | 9.03 | 9.11 | 9.2 | 9.29 | 9.4 | 9.52 | 9.64 | 9.76 | 9.88 | 10.02 | 10.16 | 10.3 | 10.46 | 10.62 | 10.78 | 10.96 | 11.15 | 11.34 | 11.54 | 11.76 | 11.98
Source: Deloitte Analysis
Key Takeaways
Landed solar cost at MP is always higher than the projected ECR for the state
For CG, ISTS charge play a significant role. In case of ISTS waiver, the landed solar energy cost is lower than the ECR projected. However, the case is entire opposite if ISTS charges are applicable

## Slide 46: Option 3: Comparison of Cost of Energy- BOO (Rs./KWh)
For Option 3: CG demand met by CG capacity, MP demand met by capacities in MP
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost @Rs. 2.20/kwh tariff | 2.45 | 2.44 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45
CG-Solar Generation Cost @Rs. 2.50/kwh tariff | 2.77 | 2.75 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77
CG-Solar Generation Cost @Rs. 3.00/kwh tariff | 3.3 | 3.28 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
CG-Solar Generation Cost @Rs. 3.50/kwh tariff | 3.84 | 3.81 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84
CG-Solar Generation Cost @Rs. 4.00/kwh tariff | 4.37 | 4.34 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost @Rs. 2.20/kwh tariff | 7 | 7.1 | 7.24 | 7.39 | 7.54 | 7.69 | 7.85 | 8.02 | 8.2 | 8.39 | 8.59 | 8.79 | 9.01 | 9.24 | 9.48 | 9.73 | 9.99 | 10.27 | 10.56 | 10.87 | 11.19 | 11.52 | 11.88 | 12.25 | 12.64 | 13.05
MP-Solar Generation Cost @Rs. 2.50/kwh tariff | 7.33 | 7.43 | 7.58 | 7.72 | 7.87 | 8.02 | 8.18 | 8.35 | 8.53 | 8.72 | 8.92 | 9.12 | 9.34 | 9.57 | 9.81 | 10.06 | 10.32 | 10.6 | 10.89 | 11.2 | 11.52 | 11.85 | 12.21 | 12.58 | 12.97 | 13.38
MP-Solar Generation Cost @Rs. 3.00/kwh tariff | 7.88 | 7.97 | 8.13 | 8.27 | 8.42 | 8.57 | 8.73 | 8.9 | 9.08 | 9.27 | 9.47 | 9.67 | 9.89 | 10.12 | 10.36 | 10.61 | 10.87 | 11.15 | 11.44 | 11.75 | 12.07 | 12.41 | 12.76 | 13.13 | 13.52 | 13.93
MP-Solar Generation Cost @Rs. 3.50/kwh tariff | 8.43 | 8.52 | 8.68 | 8.82 | 8.97 | 9.12 | 9.28 | 9.46 | 9.63 | 9.82 | 10.02 | 10.23 | 10.44 | 10.67 | 10.91 | 11.16 | 11.43 | 11.7 | 11.99 | 12.3 | 12.62 | 12.96 | 13.31 | 13.68 | 14.07 | 14.48
MP-Solar Generation Cost @Rs. 4.00/kwh tariff | 8.98 | 9.07 | 9.23 | 9.38 | 9.52 | 9.67 | 9.84 | 10.01 | 10.19 | 10.37 | 10.57 | 10.78 | 10.99 | 11.22 | 11.46 | 11.71 | 11.98 | 12.25 | 12.55 | 12.85 | 13.17 | 13.51 | 13.86 | 14.23 | 14.62 | 15.03
Source: Deloitte Analysis
Key Takeaways
Landed solar cost at MP is always higher than the projected ECR for the state
For CG, the landed solar energy cost is lower than the projected ECR for the state

## Slide 47: Savings (Rs. Crore)- For BOO (PPA mode)
 | Option 1: Entire Capacity is in CG |  |  | Option 2: Entire Capacity is in MP |  | Option 2: Entire Capacity is in MP | Option 3: CG-Own, MP-Own | Option 3: CG-Own, MP-Own
Total Savings (Rs. Crore.) for Entire Project Tenure for Multiple Capex Scenario | CG Savings | MP Savings | MP Savings- If ISTS Charge Waived off | CG Savings | CG Savings- If ISTS Charge Waived off | MP Savings | CG Savings | MP Savings
Tariff @Rs. 2.20/ kWh | 9940.72 | -2737.10 | -287.60 | -1802.60 | 4458.80 | 272.19 | 9940.72 | 272.19
Tariff @Rs. 2.50/ kWh | 9603.86 | -2891.11 | -441.60 | -2198.28 | 4063.12 | 136.33 | 9603.86 | 136.33
Tariff @Rs. 3.00/ kWh | 9042.44 | -3147.78 | -698.27 | -2857.74 | 3403.66 | -90.09 | 9042.44 | -90.09
Tariff @Rs. 3.50/ kWh | 8481.02 | -3404.45 | -954.94 | -3517.20 | 2744.20 | -316.52 | 8481.02 | -316.52
Tariff @Rs. 4.00/ kWh | 7919.59 | -3661.12 | -1211.61 | -4176.66 | 2084.74 | -542.95 | 7919.59 | -542.95
For various Options
Source: Deloitte Analysis
Key Takeaways
Option 3 yields highest savings followed by Option 1 with ISTS charges waived
Option 2 yields lowest savings under all circumstances

## Slide 48
MODEL 3: GOVERNMENT SCHEMES (PPA-BASED) FINANCIAL EVALUATION AND FINDINGS

## Slide 49: Charges Applicable for Various Options- Government Scheme
Regulatory Charges and Losses Applicable Assuming that the Project is Connected to ISTS Grid and is located in a state other than CG or MP
Regulatory Charges & Losses Applicability | CG-Own, MP-Own | 
 | Energy to CG | Energy to MP
CG-Transmission Charge |  | 
CG-SLDC Charge |  | 
CG-Wheeling Charge |  | 
CG-Cross Subsidy Surcharge |  | 
CG-Additional Surcharge |  | 
CG-Reactive Energy Charge |  | 
CG-T&D Loss |  | 
ISTS Charge | Not Applicable for CPSU Scheme Phase II | Not Applicable for CPSU Scheme
ISTS Loss |  | Not Applicable for CPSU Scheme
MP-Transmission Charge |  | 
MP-Wheeling Charge |  | 
MP-SLDC Charge |  | 
MP-Cross Subsidy Surcharge |  | 
MP-Additional Surcharge |  | 
MP-T&D Loss |  | 
Key Takeaways
ISTS Charge is not applicable for last announced CPSU scheme in this category. However, it is not clear whether this will be applicable for future schemes

## Slide 50: Option 3: Comparison of Cost of Energy- Government Scheme Projects
For Option 3: CG demand met by CG capacity, MP demand met by capacities in MP (Options 1 & 2 are not relevant in this case)
Chhattisgarh
Madhya Pradesh
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
CG-Discom ECR | 8.22 | 8.43 | 8.59 | 8.75 | 8.91 | 9.07 | 9.24 | 9.41 | 9.59 | 9.76 | 9.94 | 10.13 | 10.31 | 10.5 | 10.7 | 10.89 | 11.1 | 11.3 | 11.51 | 11.72 | 11.94 | 12.16 | 12.38 | 12.61 | 12.84 | 13.08
CG-Solar Generation Cost @Rs. 2.20/kwh- without ISTS waiver | 8.12 | 8.6 | 8.29 | 8.42 | 8.64 | 8.78 | 8.92 | 9.07 | 9.23 | 9.4 | 9.58 | 9.76 | 9.94 | 10.13 | 10.33 | 10.54 | 10.75 | 10.96 | 11.19 | 11.42 | 11.66 | 11.9 | 12.16 | 12.42 | 12.69 | 12.97
CG-Solar Generation Cost- @ Rs. 2.20/kwh-with ISTS waiver | 4.43 | 4.54 | 4.35 | 4.35 | 4.44 | 4.44 | 4.44 | 4.44 | 4.45 | 4.47 | 4.49 | 4.5 | 4.51 | 4.52 | 4.53 | 4.55 | 4.56 | 4.57 | 4.59 | 4.6 | 4.62 | 4.64 | 4.65 | 4.67 | 4.69 | 4.7
CG-Solar Generation Cost- @Rs. 2.50/kwh without ISTS waiver | 8.44 | 8.94 | 8.61 | 8.74 | 8.96 | 9.1 | 9.24 | 9.39 | 9.55 | 9.72 | 9.9 | 10.08 | 10.26 | 10.45 | 10.65 | 10.86 | 11.07 | 11.28 | 11.51 | 11.74 | 11.98 | 12.22 | 12.48 | 12.74 | 13.01 | 13.29
CG-Solar Generation Cost- @Rs. 2.50/kwh with ISTS waiver | 4.75 | 4.88 | 4.67 | 4.67 | 4.76 | 4.76 | 4.76 | 4.76 | 4.77 | 4.79 | 4.81 | 4.81 | 4.83 | 4.84 | 4.85 | 4.87 | 4.88 | 4.89 | 4.91 | 4.92 | 4.94 | 4.96 | 4.97 | 4.99 | 5.01 | 5.02
CG-Solar Generation Cost- @Rs. 3.00/kwh without ISTS waiver | 8.97 | 9.5 | 9.14 | 9.27 | 9.49 | 9.63 | 9.77 | 9.92 | 10.08 | 10.25 | 10.43 | 10.61 | 10.79 | 10.98 | 11.18 | 11.39 | 11.6 | 11.81 | 12.04 | 12.27 | 12.51 | 12.76 | 13.01 | 13.27 | 13.54 | 13.82
CG-Solar Generation Cost- @Rs. 3.00/kwh with ISTS waiver | 5.28 | 5.44 | 5.21 | 5.2 | 5.29 | 5.29 | 5.29 | 5.29 | 5.3 | 5.32 | 5.34 | 5.35 | 5.36 | 5.37 | 5.38 | 5.4 | 5.41 | 5.43 | 5.44 | 5.46 | 5.47 | 5.49 | 5.5 | 5.52 | 5.54 | 5.55
CG-Solar Generation Cost- @Rs. 3.50/kwh without ISTS waiver | 9.5 | 10.06 | 9.68 | 9.8 | 10.02 | 10.16 | 10.3 | 10.45 | 10.61 | 10.78 | 10.97 | 11.14 | 11.33 | 11.52 | 11.71 | 11.92 | 12.13 | 12.35 | 12.57 | 12.8 | 13.04 | 13.29 | 13.54 | 13.8 | 14.08 | 14.36
CG-Solar Generation Cost- @Rs. 3.50/kwh with ISTS waiver | 5.81 | 6 | 5.74 | 5.73 | 5.82 | 5.82 | 5.82 | 5.82 | 5.83 | 5.85 | 5.87 | 5.88 | 5.89 | 5.9 | 5.91 | 5.93 | 5.94 | 5.96 | 5.97 | 5.99 | 6 | 6.02 | 6.04 | 6.05 | 6.07 | 6.09
CG-Solar Generation Cost- @Rs. 4.00/kwh without ISTS waiver | 10.04 | 10.63 | 10.21 | 10.33 | 10.55 | 10.69 | 10.83 | 10.98 | 11.14 | 11.32 | 11.5 | 11.67 | 11.86 | 12.05 | 12.25 | 12.45 | 12.66 | 12.88 | 13.1 | 13.33 | 13.57 | 13.82 | 14.07 | 14.34 | 14.61 | 14.89
CG-Solar Generation Cost- @Rs. 4.00/kwh with ISTS waiver | 6.34 | 6.56 | 6.27 | 6.27 | 6.35 | 6.36 | 6.35 | 6.36 | 6.36 | 6.38 | 6.4 | 6.41 | 6.42 | 6.43 | 6.45 | 6.46 | 6.48 | 6.49 | 6.5 | 6.52 | 6.54 | 6.55 | 6.57 | 6.58 | 6.6 | 6.62
Chart: ECR Vs Solar Landed Cost Comparison (Rs./kWh)
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
MP-Discom ECR | 6.88 | 7.06 | 7.19 | 7.32 | 7.46 | 7.6 | 7.74 | 7.88 | 8.02 | 8.17 | 8.32 | 8.48 | 8.63 | 8.79 | 8.95 | 9.12 | 9.29 | 9.46 | 9.63 | 9.81 | 9.99 | 10.18 | 10.36 | 10.56 | 10.75 | 10.95
MP-Solar Generation Cost @Rs. 2.20/kwh- without ISTS waiver | 10.82 | 11.26 | 11.32 | 11.6 | 11.89 | 12.18 | 12.49 | 12.82 | 13.15 | 13.5 | 13.87 | 14.25 | 14.64 | 15.06 | 15.49 | 15.93 | 16.4 | 16.89 | 17.4 | 17.93 | 18.48 | 19.06 | 19.66 | 20.28 | 20.94 | 21.62
MP-Solar Generation Cost- @ Rs. 2.20/kwh-with ISTS waiver | 7 | 7.18 | 7.24 | 7.39 | 7.54 | 7.69 | 7.85 | 8.02 | 8.2 | 8.39 | 8.59 | 8.79 | 9.01 | 9.24 | 9.48 | 9.73 | 9.99 | 10.27 | 10.56 | 10.87 | 11.19 | 11.52 | 11.88 | 12.25 | 12.64 | 13.05
MP-Solar Generation Cost- @Rs. 2.50/kwh without ISTS waiver | 11.15 | 11.6 | 11.66 | 11.94 | 12.22 | 12.52 | 12.82 | 13.15 | 13.48 | 13.83 | 14.2 | 14.58 | 14.97 | 15.39 | 15.82 | 16.27 | 16.73 | 17.22 | 17.73 | 18.26 | 18.81 | 19.39 | 19.99 | 20.61 | 21.27 | 21.95
MP-Solar Generation Cost- @Rs. 2.50/kwh with ISTS waiver | 7.33 | 7.52 | 7.58 | 7.72 | 7.87 | 8.02 | 8.18 | 8.35 | 8.53 | 8.72 | 8.92 | 9.12 | 9.34 | 9.57 | 9.81 | 10.06 | 10.32 | 10.6 | 10.89 | 11.2 | 11.52 | 11.85 | 12.21 | 12.58 | 12.97 | 13.38
MP-Solar Generation Cost- @Rs. 3.00/kwh without ISTS waiver | 11.71 | 12.17 | 12.21 | 12.49 | 12.77 | 13.07 | 13.38 | 13.7 | 14.03 | 14.38 | 14.75 | 15.13 | 15.53 | 15.94 | 16.37 | 16.82 | 17.28 | 17.77 | 18.28 | 18.81 | 19.36 | 19.94 | 20.54 | 21.16 | 21.82 | 22.5
MP-Solar Generation Cost- @Rs. 3.00/kwh with ISTS waiver | 7.88 | 8.08 | 8.13 | 8.27 | 8.42 | 8.57 | 8.73 | 8.9 | 9.08 | 9.27 | 9.47 | 9.67 | 9.89 | 10.12 | 10.36 | 10.61 | 10.87 | 11.15 | 11.44 | 11.75 | 12.07 | 12.41 | 12.76 | 13.13 | 13.52 | 13.93
MP-Solar Generation Cost- @Rs. 3.50/kwh without ISTS waiver | 12.26 | 12.73 | 12.76 | 13.04 | 13.32 | 13.62 | 13.93 | 14.25 | 14.59 | 14.94 | 15.3 | 15.68 | 16.08 | 16.49 | 16.92 | 17.37 | 17.84 | 18.32 | 18.83 | 19.36 | 19.91 | 20.49 | 21.09 | 21.72 | 22.37 | 23.05
MP-Solar Generation Cost- @Rs. 3.50/kwh with ISTS waiver | 8.43 | 8.65 | 8.68 | 8.82 | 8.97 | 9.12 | 9.28 | 9.46 | 9.63 | 9.82 | 10.02 | 10.23 | 10.44 | 10.67 | 10.91 | 11.16 | 11.43 | 11.7 | 11.99 | 12.3 | 12.62 | 12.96 | 13.31 | 13.68 | 14.07 | 14.48
MP-Solar Generation Cost- @Rs. 4.00/kwh without ISTS waiver | 12.81 | 13.3 | 13.31 | 13.59 | 13.87 | 14.17 | 14.48 | 14.8 | 15.14 | 15.49 | 15.85 | 16.23 | 16.63 | 17.04 | 17.47 | 17.92 | 18.39 | 18.87 | 19.38 | 19.91 | 20.46 | 21.04 | 21.64 | 22.27 | 22.92 | 23.6
MP-Solar Generation Cost- @Rs. 4.00/kwh with ISTS waiver | 8.98 | 9.21 | 9.23 | 9.38 | 9.52 | 9.67 | 9.84 | 10.01 | 10.19 | 10.37 | 10.57 | 10.78 | 10.99 | 11.22 | 11.46 | 11.71 | 11.98 | 12.25 | 12.55 | 12.85 | 13.17 | 13.51 | 13.86 | 14.23 | 14.62 | 15.03
Source: Deloitte Analysis
Key Takeaways
ISTS charge plays a key role in both the states, while in CG, if ISTS is waived the solar landed cost is always lower than projected ECR. For MP it is always higher than the projected ECR.

## Slide 51: Savings (Rs. Crore)- For Government Scheme Projects (PPA Mode)
 | Chhattisgarh Savings | CG Savings- If ISTS Charge Waived off | Madhya Pradesh Savings | MP Savings- If ISTS Charge Waived off
Total Savings (Rs. Crore.) for Entire Project Tenure for Multiple Capex Scenario | CG Savings- If ISTS Charge is not Waived off | CG Savings- If ISTS Charge Waived off | MP Savings- If ISTS Charge is not Waived off | MP Savings- If ISTS Charge Waived off
Tariff @Rs. 2.20/ kWh | 1198.45 | 7459.85 | -2302.50 | 124.31
Tariff @Rs. 2.45/ kWh (CPSU Ph-II Scheme where ISTS Charge is waived off) | NA | 7160.74 | NA | 29.99
Tariff @Rs. 2.50/ kWh | 839.52 | 7100.92 | -2442.92 | 6.59
Tariff @Rs. 3.00/ kWh | 241.29 | 6502.69 | -2676.95 | -227.44
Tariff @Rs. 3.50/ kWh | -356.94 | 5904.46 | -2910.98 | -461.48
Tariff @Rs. 4.00/ kWh | -955.17 | 5306.23 | -3145.02 | -695.51
For various Options
Source: Deloitte Analysis
Key Takeaways
For Government scheme projects, CG will have savings under both the cases, when ISTS charge is waived or not-waived. However, MP is not expected to have any savings in this case under various tariff scenarios

## Slide 52
COMPARISON OF FINANCIAL GAINS OF DIFFERENT MODELS

## Slide 53: Comparison of Various Business Models based on the Financial Savings
Note: Capex Options are Taken @80:20 Debt: Equity Ratio as the Equity IRRs are highest for the case and this being a market-prevalent practice | Location Options for Implementation | Option 1: Entire Capacity is in CG |  |  |  |  | Option 2: Entire Capacity is in MP |  |  |  |  | Option 3: CG-Own, MP-Own |  | 
Business Models | Total Savings (Rs. Crore.) for Entire Project Tenure for Multiple Capex / Tariff Scenario | CG Savings | MP Savings | MP Savings- If ISTS Charge Waived off | TOTAL SAVINGS (CG+MP) | TOTAL SAVINGS (CG+MP) (if ISTS Charge is Waived) | CG Savings | CG Savings- If ISTS Charge Waived off | MP Savings | TOTAL SAVINGS (CG+MP) | TOTAL SAVINGS (CG+MP) (if ISTS Charge is Waived) | CG Savings | MP Savings | TOTAL SAVINGS (CG+MP)
Capex Own Land | Capex Own Land-Base Case Capex | 9662 | -2144 | 305 | 7518 | 9968 | -795 | 5466 | 880 | 85 | 6347 | 9662 | 880 | 10542
 | Capex Own Land-10% Discounted Capex | 9894 | -2038 | 412 | 7856 | 10306 | -523 | 5739 | 974 | 451 | 6713 | 9894 | 974 | 10868
Capex Others' Land | Capex Others' Land-Base Case Capex | 9590 | -2177 | 273 | 7413 | 9863 | -896 | 5365 | 846 | -51 | 6211 | 9586 | 850 | 10436
 | Capex Others' Land-10% Discounted Capex | 9822 | -2071 | 379 | 7751 | 10201 | -624 | 5638 | 939 | 315 | 6577 | 9818 | 943 | 10761
BOO | BOO-Tariff @Rs. 2.20/ kWh | 9941 | -2737 | -288 | 7204 | 9653 | -1803 | 4459 | 272 | -1530 | 4731 | 9941 | 272 | 10213
 | BOO-Tariff @Rs. 3.00/ kWh | 9042 | -3148 | -698 | 5895 | 8344 | -2858 | 3404 | -90 | -2948 | 3314 | 9042 | -90 | 8952
 | BOO-Tariff @Rs. 4.00/ kWh | 7920 | -3661 | -1212 | 4258 | 6708 | -4177 | 2085 | -543 | -4720 | 1542 | 7920 | -543 | 7377
GOI-Scheme | GOI-Scheme Mode_Tariff @Rs. 2.45/ kWh (CPSU Scheme where ISTS Charge is waived off) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7161 | 30 | 7191
Key Takeaways
Capex-model implementation on own land has the highest amount of savings (BOO-based Rs. 2.20/kWh has similar savings but less certainty to discover this tariff through bidding)
Option 3, i.e. CG-Own and MP-Own option for implementation has the highest amount of savings compared to others
Overall ranking based on Financial and Implementation Risks





## Slide 54: Comparison of Risks of Different Models

## Slide 55: Comparison of Various Business Models based on the Risk and Implementation Factors
Overall ranking based on Financial and Implementation Risks |  |  |  | 
Key Takeaways
For Non-Captive modes (i.e., for BOO and Government-scheme modes), risks are mostly low/absent since the projects will be executed by developers and SECL will get the power at discovered/agreed tariffs. Risk for SECL will be the lowest under these models.
Under BOO mode, since the project will be located in CG or MP, substation availability risk might be prevalent for the Developer due to potential challenge for land-availability near sub-stations. However, such risk will be for the Developer and not for SECL.
For Captive project in Other’s land, SECL will need to find sub-stations will spare evacuation capacities and available land parcels in the vicinity. There can be potential risk for SECL for availability of the same.
For Government scheme projects, risks are lowest, followed by BOO mode. Amongst two options of Capex model, the Captive/ Capex model plant on own land has lower risk since the risk for land acquisition is absent under this model.
Business Models -> | Model 1: Captive Mode |  | Model 2: BOO Mode (PPA) | Model 3: Government Scheme PPA
Land Ownership -> | Own Land | Others’ Land |  | 
Upfront Capex for SECL | High | High | Absent | Absent
Land Acquisition Risk | Absent | High | Absent | Absent
Project Execution Risk | High | High | Absent | Absent
Interest Rate Variation Risk for Debt | High | High | Absent | Absent
Substation Availability Challenges | High | Moderate | Low | Lowest
Plant Performance Risk | High | High | Absent | Absent

## Slide 56: Land Assessment

## Slide 57: Land Parcels Preferability Assessment (1/2)
Chart: 
| 3 | 15 | 25 | 25 | 17 | 8 | 25 | 20 | 17 | 32 | 60
 | 29.35 | 131.8155 | 32.8125 | 1.875 | 1.7787 | 9.6562 | 5.6875 | 6.1625 | 5.7901 | 0.9875 | 9.775
Land Parcels in Chhattisgarh
Identification of preferred Land Parcels of SECL in Chhattisgarh
Potential Size of the Plant (in MW)
Approx. Distance from Sub-station (in km)
Kumda, 0%
Ketki, 1.3%
Bisrampur, -1.5%
Standard Distance of Grid
Tier 1 Land
Suitable for > 50 MW capacity
Tier 2 Land
Suitable for 20-50 MW capacity
Mine Name,
% increase of Capex from base-case
Legends
Note:
Per km increase of distance from sub-station results in increase of Capex by 0.13% compared to base case where sub-station is located at around 15 km from the plant
Larger sized plants are preferable as the BOS cost, especially the transmission evacuation infrastructure cost is distributed per MW basis and in case of smaller plants, the cost is redundant and the per MW capex increases
CSEB, 132/33kV SS
CSEB, 132/33kV SS
CSEB, 132/33kV SS

## Slide 58: Land Parcels Preferability Assessment (2/2)
Chart: 
| 15 | 12 | 25 | 31 | 2 | 19 | 28.5 | 4 | 15.5
 | 37.5 | 6.875 | 95.8006 | 26.25 | 38 | 110.4606 | 38 | 153.75 | 96.25
Land Parcels in Madhya Pradesh
Identification of preferred Land Parcels of SECL in Madhya Pradesh
Potential Size of the Plant (in MW)
Approx. Distance from Sub-station (in km)
Burhar, -1.5%
Dhanpuri OCM, 0.1%
Kotma,
-1.6%
Kurja, 1.3%
Pinoura, 0.5%
Bijuri,
0%
Standard Distance of Grid
Tier 1 Land
Suitable for >50 MW capacity
Tier 2 Land
Suitable for 20-50 MW capacity
Mine Name,
% increase of Capex
Legends
Note:
Per km increase of distance from sub-station results in increase of Capex by 0.13% compared to base case where sub-station is located at around 15 km from the plant
Larger sized plants are preferable as the BOS cost, especially the transmission evacuation infrastructure cost is distributed per MW basis and in case of smaller plants, the cost is redundant and the per MW capex increases
MPPTCL, 132/33kV Kotma SS
MPPTCL, 132/33kV Kotma SS
MPPTCL, 132/33kV Kotma SS
MPPTCL, 132/33kV Manthar SS
MPPKVVP, 33/11 Burhar SS
MPPKVVS, 33/11 Chachai SS
Mine Name,
% increase of Capex*
*Mines where nearby sub-stations are less than 132 kV, as capacity above 15MW should be connected to 132 kV SS, as per regulations and these mines have at least 30 MW capacity lands available. Therefore, nearby Sub-stations of higher voltage should be checked with STU/ Discoms

## Slide 59: Assessment of Land Requirement vis-à-vis Land Availability (1/2)
Mode | Particulars | Capacity (MW) | Land required (acres)
Self-Consumption: Capex mode (i.e., Captive) – CG-own MP-own | Solar installed capacity required in Chhattisgarh | 210 | 841.85
 | Solar installed capacity required in MP | 85 | 339.52
Surplus Sale | Solar installed capacity required in Chhattisgarh / MP | 550 | 2198.68
Total |  | 845 | 3380.05
Requirement of Land
Availability of Land *
State | Area | Project | Land available (acres) | Approx. distance from nearest sub-station (km) | Possible capacity of solar project (MW)
Chhattisgarh | Bisrampur | Bisrampur OCM, Colony | 117.50 | 3 | 29
 |  | Kumda & Jainagar | 527.30 | 15 | 132
 |  | Jainagar | 131.25 | 25 | 33
 | Sub-total Chhattisgarh |  | 776.05 |  | 194
Madhya Pradesh | Hasdeo | Bijuri UG | 150.00 | 38 | 15
 |  | Kurja UG | 383.20 | 16 – 34 | 96
 | J&K | Kotma West Colliery | 152.96 | 2 | 38
 | Johilla | Pinoura ug | 441.84 | 19 | 110
 | Sohagpur | Sharda OC/HW | 615.00 | 154 | 12
 |  | Dhanpuri OCM | 385.00 | 15.5 | 96
 | Sub-total Madhya Pradesh |  | 2128.00 |  | 367
 | Total |  | 2904.05 |  | 561
* Preferred land parcels as identified in previous slides; The remaining land parcels available with SECL are either smaller (<10 MW) or are far from sub-stations (30 km)

## Slide 60: Assessment of Land Requirement vis-à-vis Land Availability (2/2)
Land available in Chhattisgarh (acres) | Land required for solar plant for self-consumption in Chhattisgarh (acres) |  | Land available in MP (acres) | Land required for solar plant for self-consumption in MP (acres) | Land required for solar plant for surplus sale (acres)
Shortfall of 65.80 acres of land
Shortfall of 410.20 acres of land
Key Takeaways
Area of land available in Chhattisgarh can only cater the solar plant for self-consumption, with a shortfall of 65.80 acre.
Area of land available in Madhya Pradesh can cater the entire solar capacity required for self-consumption and then part of the solar capacity for surplus sale, with a shortfall of 410.20 acre.
SECL needs to first undertake technical assessment to evaluate suitability of the available land-parcels for solar power generation. For the balance shortfall land parcels, SECL may look to procure from suitable land from govt / private owners as available.

## Slide 61
COMPARISON OF LAND AVAILABILITY FOR DIFFERENT MODELS

## Slide 62: Comparison of Various Business Models based on the Land Availability
Key Takeaways
For Government scheme projects, land availability risks are lowest. However, amongst Capex model (for captive), Own land option seems to be the most viable option as MP already has sufficient land and CG has some shortfall, which can be procured from private parties. For BOO mode project land risk is similar to that for own-land based captive project, since BOO developers will have to identify suitable lands.
The suitability of available own land and their proximity to grid sub-station having adequate evacuation capacity need to be assessed
Business Models -> | Model 1: Captive Mode |  | Model 2: BOO Mode (PPA) | Model 3: Government Scheme PPA
Land Ownership -> | Own Land | Others’ Land |  | 
Land Availability |  |  |  | 

## Slide 63: Procedural Requirements

## Slide 64
REGISTRATION, CONNECTIVITY AND OPEN ACCESS PROCEDURES FOR CHHATTISGARH

## Slide 65: Procedure for NOC / Registration of Solar Power Projects in Chhattisgarh
Clause 12 and 13 of the Policy – Identification of CREDA as Nodal Agency and single-window clearance agency will assist and guide the Project Developers and will undertake necessary activities to achieve the objectives of the Policy.
CREDA – Nodal Agency as per Chhattisgarh Solar Energy Policy 2017-27
Salient aspects of the Application to be filed before CREDA for NOC / Registration of the Solar Power Project:
Application procedure for Grid Interactive Solar PV Power Generation Projects before CREDA
General information of the applicant entity
Experience of applicant entity in Renewable Energy sector
Information regarding the proposed project, e.g., capacity, location, land, cost, place of evacuation, etc.
Technical details of project (incl. modules, PCU, mounting arrangements, evacuation infra, etc.)
Declaration to be submitted by applicant entity on fulfilment of technical/performance/statutory compliances
Payment of non-refundable processing fee of Rs. 25000/MWp + GST
CREDA will grant NOC to the applicant based on the application submitted

## Slide 66: Criteria for Voltage-level of Connectivity (1/2)
For power injection by a Captive Power Plant
As per Chhattisgarh State Electricity Regulatory Commission (Connectivity and Intra-State Open Access) Regulations, 2011 and amendments
Reg. 10(1) “The voltage level for injection of power by a generating station/captive generating plant to the intra-state transmission system and distribution system with reference to quantum of injected power shall be as specified in the State Grid Code.”
  Provisions of the Chhattisgarh State Electricity Grid Code 2011:
  Reg. 4.2.1 “The voltages at which a generating station may be connected with the grid of transmission or distribution licensee (as applicable) can be 400, 220, 132 or 33 KV. The connection point/interface point shall be the point at the sub-station of the licensee system where power is injected. The metering point shall be at the connection point / interface point.
  Following are the prescribed quantum for injection of power to the state grid with reference to voltage of injection: -
  Note:
  Under special circumstances, any deviations from the above limits may be considered by the licensee subject to technical feasibility and specific approval by the Commission. Subject to fulfillment of minimum technical requirement of meter as specified at clause no. 8.6 of this code.”
Sl. No. | Voltage of Injection | Maximum Quantum of power that can be injected into grid
1 | 33 KV | Up to 15 MVA
2 | 132 KV | Up to 75 MVA for single circuit and 150 MVA for double circuit
3 | 220 KV | Up to 200 MVA for single circuit and 400 MVA for double circuit

## Slide 67: Criteria for Voltage-level of Connectivity (2/2)
For power drawal by an Open Access Consumer
As per Chhattisgarh State Electricity Regulatory Commission (Connectivity and Intra-State Open Access) Regulations, 2011 and amendments
Reg. 10(2) “The voltage level for drawl of power by a consumer from the intra-state transmission system and distribution system (i.e., sum of quantum of open access power and contract demand with licensee) shall be as specified in the Supply Code.”
  Provisions of the Chhattisgarh State Electricity Supply Code 2011 and its amendments:
  Reg. 12.7 “The voltage level-wise prescribed quantum of power for drawal by a consumer (including captive consumer) from the intra-State transmission system and distribution system (i.e., sum of quantum of open access power and contract demand with licensee) shall be as specified in clause 3.4 of this Supply Code.”
  Reg. 3.4 “The supply voltage-wise minimum and maximum contract demands shall normally be as follows:
  Provided that due to technical reasons, the licensee may relax above provision after due approval of the Commission.”
Supply Voltage | Minimum Contract Demand | Maximum Contract Demand
230 volts | - | 3 KW
440 volts | Above 3 KW | Up to 150 HP or 112 KW
11 KV | 60 KVA | 500 KVA
33 KV | 60 KVA | 15000 KVA
132 KV | 4000 KVA | 40000 KVA
220 KV | 15000 KVA | 150000 KVA

## Slide 68: Procedure and Timeline for Application for Connectivity (1/2)
Activities | Timeline
Submission of Application by applicant as per prescribed format to Nodal Agency (STU) along with details e.g., proposed geographical location of the intra-State requester, quantum of maximum power to be interchanged, etc. and payment of Application fee | --
Processing of application and conductance of necessary interconnection study by Nodal Agency | --
Informing feasibility by STU to applicant | 30 working days after receipt of the application
Issue of demand note of estimate charges for network augmentation work | 60 working days after issue of notice of feasibility
Time frame for execution of connectivity – as per Chhattisgarh State Electricity Supply Code 2011 clause 4.58 3(c) and (d): | 
Completion time of extension work after payment by applicant as per demand note | 180 days after payment
Serving of connection after payment of necessary charges and execution of agreement by the applicant subject to receipt of clearance from Chief Electrical Inspector after completion of extension work | 30 days after completion of extension work
As per Chhattisgarh State Electricity Regulatory Commission (Connectivity and Intra-State Open Access) Regulations, 2011 and amendments
Connectivity with STU
Every connection of the applicant’s system to the STU shall be covered by a connection agreement between the applicant and STU

## Slide 69: Procedure and Timeline for Application for Connectivity (2/2)
Activities | Timeline
Submission of Application by applicant as per prescribed format to Nodal Agency (Discom) along with details e.g., proposed geographical location of the intra-State requester, quantum of maximum power to be interchanged, etc. and payment of Application fee | --
Processing of application and conductance of necessary interconnection study by Nodal Agency | --
Time frame for execution of connectivity – as per Chhattisgarh State Electricity Supply Code 2011 clause 4.58 2(a) to (d): | 
Informing feasibility by Discom to applicant | 15 working days after receipt of the application form
Issue of demand note of estimate charges for network augmentation work | 30 days after issue of notice of feasibility
Completion time of extension work after payment by applicant as per demand note and finalization of agreement | 90 days after payment
Issue of three months notice after completion of extension work by the licensee with installation of meter and metering equipment | 7 days after completion of extension work
Release of load after completion of extension work by licensee and submission of clearance from Electrical Inspector by the applicant | 7 days after completion of extension work
As per Chhattisgarh State Electricity Regulatory Commission (Connectivity and Intra-State Open Access) Regulations, 2011 and amendments
Connectivity with Discom
Every connection of the applicant’s system to the Discom shall be covered by a connection agreement between the applicant and Discom

## Slide 70: Application Fee for Connectivity in Chhattisgarh
Max. Quantum of Power to be injected / offtaken into / from Intra-state Transmission system | Application fee (Rs in lakhs)
1 MW and above and up to 50 MW | 2
More than 50 MW and up to 250 MW | 4
More than 250 MW and up to 1000 MW | 6
More than 1000 MW | 9
Max. Quantum of Power to be injected / offtaken into / from Distribution system | Application fee (Rs in lakhs)
15 MW and below | 2
As per Chhattisgarh State Electricity Regulatory Commission (Connectivity and Intra-State Open Access) Regulations, 2011 and amendments
Connectivity with STU
Connectivity with Discom

## Slide 71: Provisions regarding Evacuation Infrastructure
As per Chhattisgarh Solar Energy Policy 2017-27 [Clause 9(f)]
Evacuation line from the solar power plant’s switchyard to the grid substation of STU/Discom shall be laid by the STU/Discom at the cost of the project developer.
If the project developer wishes to lay evacuation line by himself, he can do so either under the supervision of STU/Discom by paying the supervision charges to STU/Discom, or under own supervision without paying the supervision charges.
Solar power developer shall be permitted to construct lines at its own cost upon receiving confirmation of availability of technical capability of STU/Discom network for evacuation of the power. For this purpose, STU/Discom shall assess the availability of technical capability of STU/Discom network within 30 working days of receipt of application.
As per Chhattisgarh State Electricity Regulatory Commission (Connectivity and Intra-State Open Access) Regulations, 2011 and amendments [Reg. 10(3)(i)e]
Generating station (including Captive Generating Plant) will bear cost of interconnection, in case the generating station is the requestor.
The nodal agency (STU/Discom) shall intimate the timeframe for completion of the dedicated transmission line, if it is to be executed by licensee.
In case the line work is to be executed by the requester, the broad design features of the dedicated transmission line and other technical specifications can be provided by nodal agency on payment of necessary charges.

## Slide 72: Categories and Eligibility Criteria for Open Access
Category | Description
Long-term open access | Right to use the intra-State transmission / distribution system for a period exceeding 12 years but not exceeding 25 years
Medium-term open access | Right to use the intra-State transmission / distribution system for a period exceeding 1 year but not exceeding 7 years
Short-term open access | Open access for a period up to one (1) month at one time
As per Chhattisgarh State Electricity Regulatory Commission (Connectivity and Intra-State Open Access) Regulations, 2011 and amendments
Categories of Open Access Customers
Allotment Priority
Reg. 8
“(1) A distribution licensee shall have the highest priority in the allotment of open access capacity whether in the long-term or medium term or short term open access.
(2) The applicant seeking long-term open access shall have priority over the applicant seeking medium-term open access for use of the intra-State transmission system and/or distribution system
(3) The applicant seeking long-term open access and the medium-term open access shall have priority over the short-term open access for use of the intra-State transmission system and/or distribution system”
Eligibility for Open Access
Applicant seeking open access for one (1) MW and above shall be eligible for open access
Bulk consumers who are not connected through dedicated feeders shall not be allowed open access unless exempted by the Commission for reasons to be recorded in writing (“Bulk consumer” means a consumer who avails supply at voltage of 33 KV and above)
Given the long-term nature of the solar power project, Long-term Open Access will be the preferred choice for SECL

## Slide 73: Nodal agency, Application fee, Documents and Time-frame for Long-Term Open Access in Chhattisgarh
Inter-se location of drawal and injection point | Nodal agency | Application fee (Rs. in lakhs) | Documents to accompany the application | Time frame for disposal of application (days from the receipt of application)
Both in the network of STU | STU | Rs. 2 lakh | Proof of payment of Application fee, Bank Guarantee, PPA or Sale purchase agreement of power In case of generating station or consumer not already connected to grid, documentary evidence for completion of the connectivity showing that the same shall be completed before intending date of LTOA. Declaration that there is no existing agreement for the capacity(quantum of power) for which open access is sought | 90 working days. Disposal of application shall mean sanction of LTOA.
The injection and drawl point is at intra-state transmission system and distribution licensees system respectively, or vice versa | STU | Rs. 4 lakh + (application fee for consent of distribution licensee) Rs. 2 lakh | Same as above. Additional requirement of consent of distribution licensee | 90 working days
Both within the same Distribution licensee but there is involvement of state transmission network in conveyance of electricity | STU | - do - | - do - | - do -
Both within the same Distribution licensee and there is no involvement of state transmission network | Concerned Distribution Licensee | Rs. 2 lakh | - do - | - do -

## Slide 74: Nodal agency, Application fee, Documents and Time-frame for Long-Term Inter-State Open Access (i.e. power interchange with other state)
Inter-se location of drawal and injection point | Nodal agency | Application fee (Rs. in lakhs) | Documents to accompany the application | Time frame for disposal of application (days from the receipt of application)
In different States (inter-State open access) | CTU | As per Central Commission’s Regulation | Proof of payment of Application fee, PPA or Sale-purchase agreement of power In case of generating station not already connected to grid, documentary evidence for completion of the connectivity showing that the same shall be completed before intending date of LTOA Consent from concerned SLDCs and Distribution licensees as applicable Declaration that there is no existing agreement for the capacity for which open access is sought. Other documents as specified by Central Commission. | As per Central Commission’s Regulation

## Slide 75: Other Salient Aspects in relation to Long-Term Open Access in Chhattisgarh
Applicant needs to notify to Nodal Agency exact supply-source / offtake-destination at least 3 years (or the time taken for system augmentation, whichever is less) prior to the intended date of availing LTOA.
Bank Guarantee: The application shall be accompanied by a bank guarantee of Rs 10,000/- (ten thousand) per MW of the total power to be transmitted. The bank guarantee shall be in favour of the nodal agency, in the manner laid down under the detailed procedure.
System studies by Nodal Agency: Upon receipt of Application, Nodal Agency will assess if augmentation to the existing intra-State transmission system and/or distribution system is required, and the same will be intimated to the applicant.
Both injection and drawal points are in the network of STU: Applicant shall sign an agreement with STU.
Injection and drawl points are at intra-state transmission system and distribution licensees system respectively or vice-versa: Tripartite agreement with STU and distribution licensee.
Both injection and drawl points are within the same Distribution licensee and there is no involvement of state transmission network: Applicant shall sign an agreement with the Distribution licensee.
Both injection and drawl points are within the same Distribution licensee but there is involvement of state transmission network in conveyance of electricity: Tripartite agreement with STU and distribution licensee.
Long-term Open Access Agreement

## Slide 76
REGISTRATION, CONNECTIVITY AND OPEN ACCESS PROCEDURES FOR MADHYA PRADESH

## Slide 77: Procedure for Registration and Administrative Approval for Solar Power Projects in Madhya Pradesh
Activities | Timeline
Submission of application by applicant (developer) in specified format to nodal agency (Office of Commissioner, New and Renewable Energy, Government of MP) | --
Issuance of demand note by nodal agency to applicant for depositing the requisite processing fee | Within 15 days of submission of application with all documents
Payment of processing fee of Rs. 1 lakh/MW by applicant within 15 days from issuance of demand note | Within 15 days from issuance of demand note
Administrative approval by Government of Madhya Pradesh and registration of project | Within 30 days from date of submission of all documents
Submission of project detail documents such as DPR, land-related document (Letter of land possession/Land use permission/allotment), implementation plan, performance guarantee, etc. by applicant [For projects set up on government land, submission of Performance Bank Guarantee @Rs. 5 lakh/MW by developer; In case of private land, developer is exempted from submitting any performance guarantee] | Within 3 months from date of registration / GoMP administrative approval
Financial closure ** | Within 11 months from date of GoMP administrative approval
Project commissioning ** | Within 17 months from date of GoMP administrative approval
As per the Policy for Implementation of Solar Power Based Projects in Madhya Pradesh, 2012
** The Policy for Implementation of Solar Power Based Projects in Madhya Pradesh, 2012 provides for extension of the timeline for financial closure and project commissioning by 6 months, provided Developer is able to provide adequate proof for reasons of delay being beyond the control of Developer

## Slide 78: Capacity criteria and Provisions for construction of Evacuation Infrastructure in respect of Solar Power Projects in Madhya Pradesh
As per the Policy for Implementation of Solar Power Based Projects in Madhya Pradesh, 2012
Capacity Cap of single solar PV project
Particulars | Minimum Capacity (MW) | Maximum Capacity (MW)
For solar PV project to be installed on government land | 0.025 | 100
For solar PV project to be installed on private land | No capacity cap | 
Evacuation Infrastructure
Solar Power Developer shall be responsible for laying of power evacuation line from generating station to nearest substation / interconnection point
Developer shall also be responsible for interconnection arrangement which includes transformer panel, protections, metering etc, at the substation or interconnection point
STU / Discom may take up construction and O&M of the evacuation infrastructure work at the cost of the Developer
Alternately, Developer upon approval of STU / Discom can also carry out the construction work by paying supervision charges as applicable
Sub-station augmentation, if necessary, will be carried out by STU / Discom

## Slide 79: Criteria for Voltage-level of Connectivity
As per MPERC (Terms and Conditions for Intra-State Open Access in Madhya Pradesh) Regulations, (Revision-I), 2021
Reg. 7.1 “The voltage of inter-connection shall be as per the MP Electricity Supply Code, 2021, as amended/revised from time to time.
  Provisions of the Madhya Pradesh Electricity Supply Code 2021:
  Reg. 34 “The supply voltage for different contract demands shall normally be as follows:
  Provided that if the licensee is satisfied that there are sufficient grounds for deviation in the norms above stated and such deviation is technically feasible, it may grant the same for reasons to be recorded in writing.”
  As per Madhya Pradesh Electricity Grid Code (Revision-II), 2019
  For connectivity with STU: Reg. 5.14.4 “IPPs, CPPs, EHV Consumers and Open access users – Voltage may be 220/132 kV or as agreed with STU.”
Supply Voltage | Minimum Contract Demand | Maximum Contract Demand
11 KV | 50 KVA | 300 KVA
33 KV | 100 KVA | 10000 KVA
132 KV | 5000 KVA | 50000 KVA
220 KV or more | 40000 KVA | ---

## Slide 80: Procedure and Timeline for Application for Connectivity
Activities | Timeline
Submission of application by applicant to STU in stipulated format with all relevant details including details of capacity, protection and metering, switchyard, DPR, studies regarding connectivity, etc. | --
Formal offer by STU specifying any need for network augmentation | Within 60 days of receipt of application
As per Madhya Pradesh Electricity Grid Code (Revision-II), 2019
Connectivity with STU
As per Madhya Pradesh Electricity Supply Code 2021
Connectivity with Discom
Reg. 4.65 “In cases where extension of line or sub-station or installation of plant or installation of transformer or enhancement in transformation capacity of sub-station or enhancement of capacity of lines is required, the connection shall be served within the following time limits (subject to Force Majeure conditions) after receipt of application complete in all respects and payment of necessary charges and completion of all formalities such as execution of agreement etc.:
Type of service connection | Time limit for providing service connection to the consumer
HT connection (≤ 33 KV) | 90 days from the date access is made available to the licensee
EHT connection (> 33 KV) | 180 days from the date access is made available to the licensee

## Slide 81: Connection Agreement
As per Madhya Pradesh Electricity Grid Code (Revision-II), 2019
Reg. 5.4 “A Connection Agreement (or the offer for a Connection Agreement) shall include, as appropriate, within its terms and conditions the following:
A condition requiring both parties to comply with the Grid Code.
Details of connection and/or use of system charges.
Details of any capital related payments arising from necessary reinforcement or extension of the system.
Diagram of electrical system to be connected.
General philosophy, guidelines etc. on protection.
A Site Responsibility Schedule (Appendix G).
Details of arrangement of drawl of grid energy by the user.”

## Slide 82: Categories and Eligibility Criteria for Open Access
Category | Description
Long-term open access customer | An open access customer availing intra-State open access for a period exceeding five years
Medium-term open access customer | An open access customer availing intra-State open access for a period of more than 3 months and up to 5 years
Short-term open access customer | An open access customer availing intra-State open access for a period up to 3 months
As per MPERC (Terms and Conditions for Intra-State Open Access in Madhya Pradesh) Regulations, (Revision-I), 2021
Categories of Open Access Customers
Allotment Priority
Reg. 6.1 “The allotment priority for allowing open access shall be decided in the following order of priority:
Distribution Licensee (irrespective of whether Open Access has been sought for long-term, Medium-term or Short-term);
Other Long-term Open Access Applicants;
Other Medium-term Open Access Applicants;
Other Short-term Open Access Applicants”
Eligibility for Open Access
No capacity limitation for captive open access consumers
No capacity limitation for granting open access to renewable energy generators and users
Given the long-term nature of the solar power project, Long-term Open Access will be the preferred choice for SECL

## Slide 83: Procedure for availing Long-term Open Access
As per MPERC (Terms and Conditions for Intra-State Open Access in Madhya Pradesh) Regulations, (Revision-I), 2021
Activities | Timeline
Filing of application by the prospective open access customer to the nodal agency (STU is the nodal agency) in stipulated format with details such as quantum of power, points of injection and drawal, voltage level, details of generating station, etc. [Application to be accompanied by non-refundable application fee of Rs. 1 lakh payable to STU] | --
Submission of copy of application by applicant to Discom in whose area of supply the point of drawal lies | --
Acknowledgement of the receipt of application by nodal agency | Within 1 working day of receipt
Intimation by STU whether open access can be allowed with or without system strengthening | Within 30 days of receipt of the application
Grant of open access by STU in case no system strengthening is required | - do -
In case of further system strengthening required, request by applicant to STU to carry out system studies | --
Conduction of system studies and intimation of result to applicant by STU along with cost estimates and completion schedule | Within 45 days of receipt of request
Bulk Power Transmission Agreement: Reg. 10.1 “A long-term and medium-term open access customer using transmission system shall enter into Bulk Power Transmission Agreement (BPTA) with the Transmission Licensee for use of intra-State transmission system.
Bulk Power Wheeling Agreement: Reg. 10.2 “A long-term and medium-term open access customer using distribution system shall enter into Bulk Power Wheeling Agreement (BPWA) with the Distribution Licensee for of distribution system”
Open Access Agreements

## Slide 84
COMPARISON OF PROCEDURES FOR DIFFERENT MODELS

## Slide 85: Comparison of procedures for different models
Broad Procedures / Steps | Model-1: Capex Mode (Own land) | Model-2: Capex Mode (Other’s land) | Model-3: BOO Mode (PPA Based) | Model-4: GoI Scheme (PPA Based) – yet to be tendered | Model-4a: GoI Scheme – un-tied commissioned / under-construction project
BOO bidding and award | N/A | N/A | By SECL | To be undertaken by the developer as suitable | N/A (since project is commissioned / under-construction)
NOC / Registration for solar power project | By SECL | By SECL | By BOO |  | 
EPC bidding and award | By SECL | By SECL | By BOO |  | By Developer
Procedure for obtaining grant of Connectivity and Open Access | By EPC | By EPC | By BOO/EPC |  | 
 |  |  |  |  | By Developer/EPC
Procedure for obtaining grant of Open Access | By EPC | By EPC | By BOO/EPC | By SECL | By SECL
Land acquisition | N/A | By EPC | By BOO/EPC | To be undertaken by the developer as suitable | N/A
Plant construction and commissioning | By EPC | By EPC | By BOO/EPC |  | By Developer/EPC
Overall ranking based on number of broad procedures / steps |  |  |  |  | 
Note:
Overall timeline will depend upon the time required for land acquisition, network augmentation by licensee (if any), which will depend upon ground-scenario and cannot be specified at this stage
Estimated time for selection of developer and EPC contractor will be around 1-1.5 months each, and time taken for project construction and commissioning will be around 18-24 months, as per standard industry practice. However, these timelines may vary based on ground-scenarios.
Key Takeaway: GoI Scheme-already commissioned / under-construction projects with un-tied capacities is the best option, followed by Captive projects at Own Land

## Slide 86: Assessment of Potential Avenues for Sale of Surplus Solar Energy

## Slide 87: Various Avenues for Sale of Solar Energy
Discoms Sale
ENERGY SALE TO DISCOMS IN CHHATTISGARH AND MADHYA PRADESH
Energy Banking
ENERGY BANKING WITH DISCOMS IN CHHATTISGARH AND MADHYA PRADESH
Energy Exchange
Sale Through Energy Exchange
Energy Traders
ENERGY SALE TO TRADING LICENSEES IN INDIA
Open Access Consumer
ENERGY SALE TO OPEN ACCESS CONSUMERS IN CHHATTISGARH AND MADHYA PRADESH
REC
RENEWABLE ENERGY CERTIFICATES

## Slide 88
ENERGY SALE TO DISCOMS IN CHHATTISGARH AND MADHYA PRADESH

## Slide 89: Regulatory Provisions in Madhya Pradesh for Sale of Solar Energy to Discoms (1/2)
As per Madhya Pradesh Electricity Regulatory Commission (Co-generation and generation of electricity from Renewable sources of energy) (Revision-II) Regulations, 2021
  Reg. 3.6 “The energy from all the Renewable Sources of Energy including renewable Co-generation units may be procured by the MP Power Management Company Limited (MPPMCL) on behalf of the State owned Distribution Licensees, at the tariff determined by the Commission from time to time in its Tariff Orders or at the tariff adopted by the Commission.”
  Reg. 3.7 “The Power Purchase Agreement (PPA) shall be signed between the Renewable Energy Generating company/Developer and the MP Power Management Company Limited. MPPMCL in turn will have back-to-back Power Supply Agreement with the Distribution Licensees.”
  Reg. 3.9 “Procedure for execution of Power Purchase Agreement(s) {PPAs} and Wheeling Agreement (s) {WAs}:
  The Renewable Energy Generating company/Developer shall approach the MP Power Management Company Limited with the proposal for sale of power generated from their machine(s). The proposal for sale of power shall include details of Company/Project in the applicable Format C (i) to (v) as specified in MPERC (Furnishing of Technical details by Generating Companies) Regulations, 2011.
  Simultaneously, Renewable Energy Generating company/Developer shall also approach the Transmission Licensee and the Distribution Licensee and furnish the requisite details as at (a) above, enabling them to conduct interconnection studies. If found feasible, permission shall be granted to the Renewable Energy Generating company/Developer along with an estimate of the cost of extension/bay and other charges within 30 days from the date of receipt of application with a copy to MP Power Management Company Limited. For long term access, M.P. Power Transmission Company shall grant permission, if found technically feasible, within 15 days of receipt of application.
  Thereafter, the MP Power Management Company Limited shall execute the Power Purchase Agreement(s)/ and Wheeling Agreement(s), as the case may be, within 15 days from the date of receipt of proposal for sale of power in cases where new interconnection is not required. In cases where new interconnection is required, these agreements shall be executed within 15 days of receipt of permission from the Distribution Licensee and the Transmission Licensee (as applicable).”

## Slide 90: Regulatory Provisions in Madhya Pradesh for Sale of Solar Energy to Discoms (2/2)
As per Madhya Pradesh Electricity Regulatory Commission (Co-generation and generation of electricity from Renewable sources of energy) (Revision-II) Regulations, 2021
  Reg. 4 Power Purchase Agreement
  Reg. 4.1 “The Power Purchase Agreement period will be of minimum 20 years, if not otherwise specified in the Tariff Orders, from the date of commissioning of plant. However, the agreement may be for a shorter period in case the Renewable Energy Generating company/Developer opts to supply to the Distribution Licensees after consuming the electricity for self-use/ third party sale for lesser period.”
  Reg. 4.2 “The Renewable Energy Generating company/Developers are required to get all the required statutory consents before entering into the Agreement. Such consents shall have validity for the entire period of the Agreement.”
  Reg. 4.3 “The MP Power Management Company Limited on behalf of the State-owned Distribution Licensees shall have to obtain the approval of Power Purchase Agreement from the Commission”
  Reg. 6 Open Access for Co-generation and generation from Renewable Sources of Energy
  “Any person generating electricity from Co-generation and Renewable Sources of Energy shall be eligible for Open Access, in accordance with the applicable Madhya Pradesh Electricity Regulatory Commission (Terms and Conditions for Intra-State Open Access in Madhya Pradesh) Regulations.”

## Slide 91: Projected Solar RPO shortfall for MP Discoms in future years provides potential opportunity for SECL to sale solar power to MP Discoms
As projected by MPERC in ‘MPERC Aggregate Revenue Requirement for FY 2022-23 to FY 2026-27 and Retail Supply Tariff Order for FY 2022-23’ dated 31.03.2022
Quantum of Solar RPO shortfall for MP Discoms (as projected by MPERC)
Particulars | FY 2022-23 | FY 2023-24 | FY 2024-25 | FY 2025-26 | FY 2026-27
Solar RPO (%) as per MPERC | 9% | 10% | 11% | 12% | 13%
Solar Power Purchase to fulfil RPO (MU) | 7,115.07 | 8,492.26 | 9,967.09 | 11,617.89 | 13,600.06
Solar Energy available from existing plants (MU) | 7,554.97 | 9,764.47 | 10,500.97 | 10,500.97 | 10,500.97
Solar Energy Surplus / (Shortfall) (MU) | 439.90 | 1,272.21 | 533.87 | (1,116.92) | (3,099.10)
Tariff for procurement of solar energy by MP Discoms (as projected by MPERC)
Particulars | FY 2022-23 | FY 2023-24 | FY 2024-25 | FY 2025-26 | FY 2026-27
Rates for power procurement from existing solar stations (Rs/kWh) | 3.46 | 3.22 | 3.16 | 3.16 | 3.16
Rates for procurement of shortfall solar energy (Rs/kWh) | - | - | - | 2.62 | 2.62
Opportunity may be explored with MPPMCL to assess the requirement to procure solar power by MP Discoms.
Chhattisgarh Discom however has stated during interactions that it will not buy solar power directly from any generator, and instead will buy from SECI.

## Slide 92
ENERGY BANKING WITH DISCOMS IN CHHATTISGARH AND MADHYA PRADESH

## Slide 93: Concept of Energy Banking
In banking of power, a generating plant supplies power to the discom without any financial transactions involved. The generating plant holds the option to draw back the power from the discom within a specified time period and against the charges specified under relevant regulations.
APTEL in its order dtd. 18.03.2011 in Appeal no. 98 of 2010 explained the concept of Energy Banking as under (in the context of captive wind energy generator):
    “18… Generation by Wind Energy Generators solely depends upon availability of wind at a particular velocity… It could be possible that it generates electricity when captive user does not require it. In such a case energy generator banks it with distribution licensee who supplies this energy to its consumers at applicable tariff. However, for returning the banked energy, Licensee may have to procure additional electricity from other sources. Unlike the Banks which pay interest to saving account holder, here the licensee, banker of electrical energy, earns interest on this banked energy.”
APTEL in Maharashtra State Electricity Distribution Company Limited v. Maharashtra Electricity Regulatory Commission, 2014 SCC OnLine APTEL 166, explained the concept of banking (in the context of captive wind energy generator) as under:
    “31… under which the surplus energy injected by the wind energy generator and utilized by the Distribution Licensee is considered as banked energy which is supplied back to the consumer during the period when the wind energy generation is less than the demand of the open access consumer in the same Financial Year”

## Slide 94: Regulatory Provisions in Chhattisgarh for Energy Banking (1/2)
As per Chhattisgarh State Electricity Regulatory Commission (Grid Interactive Distributed Renewable Energy Sources) (First Amendment) Regulations, 2021
  “21.1 All solar power projects shall be awarded must-run status i.e. injection from the solar power projects shall be considered as deemed to be scheduled.
  21.2 Banking facility will be available for useful life period of the project.
  21.3 Banking of 100% of energy injection after netting the generation with in-house auxiliary requirement shall be permitted for all captive and open access consumption.
  21.4 Banking charges @ 2% of banked energy shall be payable in kind. The banking year shall be from April to March.
  21.5 Banked units redeemed during normal period (5 am to 6 pm or as specified in the applicable Tariff Order) and off-peak load period (11 pm to 5 am next day or as specified in the applicable Tariff Order) shall not have any withdrawal charges. Banked energy redeemed during evening peak load period (6 pm to 11 pm or as specified in the applicable Tariff Order) shall attract peak withdrawal charges in kind which shall be 30% of energy drawn during the peak load hrs…
  21.7 The unutilized banked energy/surplus energy, if any, at the end of financial year shall be purchased by distribution licensee at lowest rooftop solar tariff discovered through competitive bidding undertaken by distribution licensee in the last financial year. If such tariff is not available, lowest tariff through competitive bidding undertaken by SECI in last financial year shall be considered.”

## Slide 95: Regulatory Provisions in Chhattisgarh for Energy Banking (2/2)
As per CSERC Revised Modality for Renewable Energy Banking, Accounting, Settlement and Wheeling
Banked Energy at the end of i-th month (Ebi) = {Egi x (1 – a) – Eci} x (1 – b) + Eb(i-1) Where,
  Egi = Energy injected for the i-th month
  Eci = Energy consumption/drawal for the i-th month (consumption end)
  Eb(i-1) = Energy Banked at the end of previous month
  a = Transmission and distribution losses as per CSERC DRE Regulations and its subsequent amendments
  b = Banking charges in kind, which is 2% as per Regulations
Settlement of energy consumed at consumer end, as per the installed ABT meter, shall be in the following priority.
  Solar energy injection after adjustment of transmission and wheeling charges in kind
  Captive energy from the captive generating plant located at distant location after adjustment of transmission and wheeling charges in kind
  Banked solar energy
  Open Access energy through Exchange or any other source
  Energy of distribution licensee

## Slide 96: Regulatory Provisions in Madhya Pradesh for Energy Banking
As per Madhya Pradesh Electricity Regulatory Commission (Co-generation and generation of electricity from Renewable sources of energy) (Revision-II) Regulations, 2021
  “Reg. 10.1…
  (i) The entire power generated from Renewable Sources of Energy during a Financial Year may be allowed for Banking:
  Provided that Renewable Energy based Captive Generating Plants, which are registered with the Distribution Licensee under Regulation 11.4 (a) of these Regulations, shall not be eligible to avail banking facility as provided under these Regulations.
  (ii) The accounting of Banking of Energy will be certified by MP Power Management Company Limited/Distribution Licensees at the end of each Financial Year.
  (iii) The quantum of banked energy will be returned at a time to be decided by the MP Power Management Company Limited/Distribution Licensees during the Financial Year by deducting 5% of the banked energy towards Banking Charges.
  (iv) If a portion of banked power still remains un-adjusted at the end of Financial Year, then such remaining power would be construed as power purchased and the payment for the same will be made by the Distribution Licensee / MP Power Management Company Limited at the rate equal to the lowest tariff rate discovered in the solar/ wind bidding, as the case may be, for the State of MP in that year. In case no rate is discovered in that year, the available lowest tariff rate discovered in the latest previous year shall be considered.”

## Slide 97: Energy Banking – Implications for SECL
SECL can bank its surplus solar energy to the discom during day-time.
During night or when captive solar power is unavailable, SECL can redeem the banked energy from discom upon deduction of banking charge and (if any) withdrawal charge, and utilize the redeemed energy for its own consumption.
Since during night-time, the redeemed banked energy will be used by SECL to meet its own consumption, SECL won’t have to pay Energy Charges to the discom for this energy consumption.
This will lead to savings in Energy Charges for SECL.
In addition, there will be an opportunity to sell the unutilized / surplus banked energy to discom at year-end at the specified tariff. If such tariff is greater than SECL’s cost of generation, such sale will be profitable for SECL.
Banking facility is subject to change by the Regulatory Commission / State Government at any point of time. For example, the Government of Andhra Pradesh has withdrawn the energy banking facility vide amendment of Solar Policy dtd. 18.11.2019.
Therefore, energy banking is associated with regulatory risk.
Opportunity for SECL
Commercial benefits for SECL
Demerit

## Slide 98
Sale Through Energy Exchange

## Slide 99: Energy Exchange
Concept of Power Exchange
Energy Exchange Trend
The concept of trading through an exchange allows traders to determine the right market price and the best consumer or seller for trade. Power exchanges or platforms for trading energy were constituted to increase competition and transparency in such markets. Hence, it can be said that power exchanges increase market transparency and reduce counterparty credit risk.
Key Purposes of Exchange:
Facilitate the trading of electricity
Developing competitive power market
transparency
liquidity
Two Operating Exchanges:
Indian Energy Exchange (IEX)
Power Exchange of India Ltd. (PXIL)
Third One is granted approval by CERC in Feb’2022
Hindustan Power Exchange Ltd (HPX)
Success factor of a PX can be measured with the following
inputs:
Number of participants in PX
Liquidity in the market
Market growth in terms of traded volume
Competitiveness of fee structure
Chart: 
| Apr'21 | May'21 | Jun'21 | Jul'21 | Aug'21 | Sep'21 | Oct'21 | Nov'21 | Dec'21 | Jan'22 | Feb'22 | Mar'22
Total Generation (MU) | 115532.35 | 103960.21 | 106405.21 | 115654.66 | 120778.01 | 108371.93 | 110803.88 | 96749.51 | 106080.38 | 108051.38 | 104230.33 | 123866.99
Total Energy Traded in Exchange (MU) | 7177.31 | 5803.48 | 6061.78 | 5837.01 | 8513.34 | 8262.12 | 8587.26 | 6180.32 | 7093.74 | 7053.73 | 7359.81 | 8084.27
Chart: Energy Traded in Exchanges During FY22 (in MU)
| IEX | PXIL
1st Qtr | 85971.55 | 42.62
Source: CERC Market Monitoring Reports for Apr ’21 to Mar ’22

## Slide 100: IEX Market Structure: Green Term Ahead Market (G-TAM)
G-TAM Structure
Contract Specifications of G-TAM
The Green-Term Ahead Market (G-TAM) is a new market segment for trading in renewable energy following the CERC approval. The new market segment features contracts such as Green-Intraday, Green-Day-ahead Contingency (DAC), Green-Daily and Green-Weekly.
Solar
Categorized in four types
G-TAM
Has both types, Solar & Non-solar
Non-Solar
Categorized in four types
Intraday
Daily
DAC
Weekly
Pay-Out
3. Daily
4. Weekly
1. Intraday
2. DAC
15 min-same day delivery
Continuous Trading
T+1
Auction
Daily
00:15-19:30
D
D-1
Energy Traded in MWh (Profile)
Contract
Trading
Pay-in
Delivery Hours
T+1
04:00-24:00
15 min- next day delivery
Trading Days
Wednesday to Friday
Trading Hours
15:00-23:30
Daily
1:00-23:00
Weekly
12:00-17:00
00:00-24:00
As per the Profile
D+1
T: Trading Day
D: Delivery Day
Source: IEX website

## Slide 101: IEX Market Structure: Green Day Ahead Market (G-DAM)
G-DAM Structure
Trading Process
Green Day ahead Market allows anonymous & double sided closed collective auction in renewable energy on the day-ahead. The Exchange now invites bids for conventional and renewable in an integrated way through separate bidding windows. The clearing takes place in a sequential manner – first in the renewable segment having the must-run status, considering the availability of the transmission corridor, followed by conventional segment.
Solar
Trading of 15-min contracts
G-DAM
Three Categories
Non-Solar
Trading of 15-min contracts
Hydro
Trading of 15-min contracts
Key Features:
Participants at either premium or discount price can use ‘Order Carry forward (OCF)’ at the time of placing bid to carry forward uncleared bids to conventional DAM
Double-sided anonymous closed bidding auction
Separate Price forming for Green power
Scheduled as RE Power
Green power at bundled
price to meet RPO
RE Seller
GDAM
Bidding of Unsold/ uncleared Bids
RE Buyer
Bid
Cleared
Scheduled as Conventional
DAM Power
Electricity at DAM ACP+
Tradeable RECs
Conv
Seller
DAM
Conv
Buyer
Bid
Cleared
Source: IEX website

## Slide 102: PXIL Market Structure: Green Term Ahead Market (G-TAM)
G-TAM Structure
Contract Specifications of G-TAM
The Green-Term Ahead Market (G-TAM) is a new market segment for trading in renewable energy following the CERC approval. The new market segment features contracts such as Green-Intraday, Green-Day-ahead Contingency (DAC), Green-Daily and Green-Weekly.
Solar
Categorized in four types
G-TAM
Has both types, Solar & Non-solar
Non-Solar
Categorized in four types
Intraday GTAM
Any-day GTAM
2. Any-day GTAM
1. Intraday GTAM
15 min slab delivery
Auction
Daily
Starts at 03:15
15 min slab delivery
Contract
Trading
Delivery Hours
Till 24:00 next day
Trading Days
Daily or Contiguous days for Single or Multiple Days
Trading Hours
Anytime
Starts at Day after Trade Date
Bilateral basis Trading
Source: PXIL website

## Slide 103: IEX Market Trends
G-DAM Trends (since inception in Oct’21)
G-TAM Trends (DAC) (for Past 12 Months)
Chart: Weighted MCP (Rs/kWh)
Chart: Sell Bid and Final Settled Volume (MWh)
Sell Bid (MWh) Non-Solar (MWh)
Sell Bid (MWh) Hydro (MWh)
Sell Bid (MWh) Hydro (MWh)
MCV (MWh) Total (MWh)
MCV (MWh) Total (MWh)
MCV (MWh) Solar (MWh)
MCV (MWh) Non-Solar (MWh)
MCV (MWh) Hydro (MWh)
Final Scheduled Volume (MWh) Total (MWh)
Final Scheduled Volume (MWh) Non-Solar (MWh)
Key Takeaways
For G-DAM, the highest weighted average tariff was Rs. 15.90/kWh, while the average tariff since inception was Rs. 5.77/kWh and the average sell bid was 6.95 GWh and settled volume was 3.42 GWh.
For G-TAM, in DAC category the highest weighted average tariff was Rs. 18.24/kWh, while the average tariff was Rs. 4.90/kWh, the total traded volume was 828 GWh for DAC mode
Source: IEX
Chart: 
Chart: 

## Slide 104: Sale through Power Exchanges– Implications for SECL
SECL can sell its surplus solar energy through energy exchanges
Sale to power traders will be commercially viable for SECL only when the selling tariff is greater than the cost of generation
The prices are highly volatile and the risk factors are high
Since, long term open access consumers get first preference over short term consumers, the availability of open access is a key challenge in such short-term sales
Opportunity for SECL
Commercial implication for SECL
Demerit

## Slide 105
ENERGY SALE TO TRADING LICENSEES IN INDIA

## Slide 106: Concept of Power Trading
Discoms, Power Exchanges, Open Access Consumers
Short-term Contract: period of the contract is up to 1 year
Long-term Contract: period of the contract is more than 1 year
  [as per CERC (Procedure, Terms and Conditions for grant of trading licence and other related matters) Regulations, 2020]
Short-term Contract: 0 paise/kWh to 7 paise/kWh
Long-term Contract: mutually decided between the Trading Licensee and the seller
[as per CERC (Procedure, Terms and Conditions for grant of trading licence and other related matters) Regulations, 2020]
Definition
Types of Contract
Trading Margin
Potential buyers from trading licensees
Trading means purchase of electricity for resale thereof (as per Electricity Act 2003)
Names of Trading Licensees | % Share in total Volume transacted by Trading Licensees |  |  |  |  |  |  |  |  |  |  | 
Names of Trading Licensees | Apr ‘21 | May ‘21 | Jun ‘21 | Jul ‘21 | Aug ‘21 | Sep ‘21 | Oct ‘21 | Nov ‘21 | Dec ‘21 | Jan ‘22 | Feb ‘22 | Mar ‘22
PTC India Ltd. | 42% | 48% | 49% | 45% | 44% | 47% | 43% | 44% | 49% | 48% | 46% | 33%
NTPC Vidyut Vyapar Nigam Ltd. | 12% | 12% | 8% | 10% | 10% | 10% | 10% | 13% | 13% | 14% | 11% | 17%
Adani Enterprises Ltd | 12% | 10% | 5% | 5% | 5% | 6% | 14% | 9% | 7% | 5% | 8% | 12%
Tata Power Trading Company (P) Ltd. | 11% | 11% | 15% | 14% | 15% | 15% | 9% | 10% | 10% | 7% | 8% | 11%
Manikaran Power Ltd. | 7% | 6% | 9% | 10% | 8% | 7% | 7% | 8% | 6% | 7% | 6% | 7%
Leading Power Traders in India and their Market Share
Source: CERC Monthly Reports on Short-term Transactions of Electricity in India

## Slide 107: Sale to Power Traders – Implications for SECL
SECL can sell its surplus solar energy through power traders.
For this, long-term contracts will be more preferable for SECL due to tariff certainty.
Sale to power traders will be commercially viable for SECL only when the selling tariff is greater than the cost of generation
Deliberations may be made with the leading power traders to understand the opportunity for power sale through the traders.
Opportunity for SECL
Commercial implication for SECL
Way Forward

## Slide 108
ENERGY SALE TO OPEN ACCESS CONSUMERS IN CHHATTISGARH AND MADHYA PRADESH

## Slide 109: Sale to Open Access Consumers – Implications for SECL
Large industrial consumers in Chhattisgarh and Madhya Pradesh
Such arrangement will be attractive for open access consumers when landed price of solar power (incl. all applicable open access charges) is less than discom energy charge
Since demand of individual consumers will not be substantial, several consumers will have to be contracted to sell sizable quantity of solar power
Managing several contracts can be challenging and cumbersome for SECL
Potential Target Segment
Commercial implication
Demerit

## Slide 110
RENEWABLE ENERGY CERTIFICATES

## Slide 111: Concept of Renewable Energy Certificate (REC)
The Certificates shall be exchanged through power exchanges or through electricity traders
The price of Certificates shall be as discovered in the Power Exchange(s) or as mutually agreed between eligible entities and the electricity traders
The Certificates once exchanged through Power Exchange(s) or through electricity traders and used for compliance of RPO by the obligated entities, shall stand redeemed
Each Certificate issued under these regulations shall represent 1 MWh of electricity generated from renewable energy sources
  [as per CERC (Terms and Conditions for Renewable Energy Certificates for Renewable Energy Generation) Regulations, 2022]
Eligibility for issuance of REC
Denomination of REC
Pricing and redemption of REC
A renewable energy generating station shall be eligible for issuance of Certificates, if it meets the following conditions:
  Tariff of such generating station, for part or full capacity, has not been either determined or adopted under section 62 (i.e. determined by Regulatory Commission) or section 63 (i.e. determined through competitive bidding) of the Act
  OR
  Electricity generated is not sold directly or through an electricity trader or in the Power Exchange, for RPO compliance by an obligated entity
  Such generating station has not availed any (i) waiver of or concessional transmission charges or (ii) waiver of or concessional wheeling charges.
  Certificates issued to a captive generating station to the extent of self consumption shall not be eligible for sale.
  [as per CERC (Terms and Conditions for Renewable Energy Certificates for Renewable Energy Generation) Regulations, 2022]

## Slide 112: REC process and recent transaction trend
Accreditation by State Agency to the Eligible Entity for REC
Registration of the Eligible Entity by Nodal Agency for REC
Issuance, exchange and redemption of REC
REC process
Recent transaction trend for Solar REC-s
Chart: 
| Nov '21 | Dec '21 | Jan '22 | Feb '22 | Mar '22
Market Clearing Volume at IEX (MU) | 253.118 | 254.98 | 193.121 | 167.447 | 251.976
Market Clearing Volume at PXIL (MU) | 63.126 | 78.907 | 60.897 | 12.59 | 26.367
Chart: 
| Nov '21 | Dec '21 | Jan '22 | Feb '22 | Mar '22
Wtd. Avg. Market Clearing Price at IEX (Rs/kWh) | 2 | 2.211 | 2.3 | 2.3 | 2.25
Wtd. Avg. Market Clearing Price at PXIL (Rs/kWh) | 2 | 2.1 | 2.4 | 2.201 | 2.205
REC pricing is capped by CERC at regulated floor price and forbearance price
During FY 21-22, there was no transaction of REC prior to Nov ’21, since the trading was postponed by APTEL in matter of the CERC Order dated 17th June 2020, fixing new floor and forbearance price for both Solar and Non-solar RECs
Market clearing volume of Solar RECs
Market clearing price of Solar RECs
Source: CERC Monthly Reports on Short-term Transactions of Electricity in India
As per CERC (Terms and Conditions for Renewable Energy Certificates for Renewable Energy Generation) Regulations, 2022

## Slide 113: Sale of REC – Implications for SECL
If SECL’s surplus solar energy is sold to exchange or trader and the tariff is not determined by any Commission or through competitive bidding, SECL will be eligible for RECs for such sale and can trade those RECs.
Selling of RECs will result in additional revenue for SECL.
Price of REC is regulated by CERC.
Therefore, revenue from sale of RECs is associated with regulatory risk.
Opportunity for SECL
Commercial implication for SECL
Demerit

## Slide 114: Comparison of Various Options for Surplus Power Selling of SECL
Overall ranking based on Financial and Implementation Risks |  |  |  |  |  | 
Key Takeaways
Energy Sale to discoms is the lowest risk option followed by Energy Banking and Sale through traders. However, the willingness and conventional practice of the discoms will play a key role in selling the surplus power sell of SECL
SECL can initiate the communication with CG-Discom and MP-Discoms for Energy Banking and initiate necessary procedure
Land Ownership -> | Energy Sale to Discoms | Energy Banking | Sell through Energy Exchanges | Sell through Trading Licensees | Sell to Open Access Consumers | Renewable Energy Certificate (REC)
Off-take / Volume Risk |  |  |  |  |  | 
Price Volatility Risk |  |  |  |  |  | 
Regulatory Risk |  |  |  |  |  | 
Open Access Availability Challenges |  |  |  |  |  | Absent
Multiple Consumer Management Risk |  |  |  |  |  | 
Overall Operational Complexity |  |  |  |  |  | 
Consumer Willingness |  |  |  |  |  | 

## Slide 115: Evaluation Summary

## Slide 116
Comparison of Models for SELF CONSUMPTION

## Slide 117: Final Rating for Comparison of the Models for Self Consumption
Overall ranking based on All Parameters |  |  |  |  | 
Key Takeaways
The overall rating is highest for Solar power purchase from projects under GOI Scheme (e.g. CPSU Ph-II) where projects are un-tied and commissioned / under-construction.
The second most preferred option is Capex Mode at Own Land (CG-Own and MP-Own) subject to availability of suitable land. The financial savings under this model is the highest.
SECL can take necessary steps to further explore these two options. Accordingly, the next steps are outlined in the subsequent sections.
Business Models -> | Model-1: Capex Mode (Own land) (CG-Own and MP-Own) | Model-2: Capex Mode (Other’s land) | Model-3: BOO Mode (PPA Based) | Model-4: GoI Scheme (PPA Based) – project yet to be tendered | Model-4a: GoI Scheme – un-tied commissioned / under-construction project
Financial Gains |  |  |  |  | 
Risk Perspective |  |  |  |  | 
Land Availability |  |  |  |  | 
Steps Required/ Timeline |  |  |  |  | 

## Slide 118: Recommendations for SECL for choice of Project Models for Self Consumption
Two models are evaluated to be the most preferred ones:
  Purchase of solar power from un-tied commissioned / under-construction solar projects under GOI-scheme (e.g. CPSU Ph-II scheme);
  Establishment of solar power plant in capex mode (i.e. captive power plant) in own land in both Chhattisgarh and Madhya Pradesh to meet captive power requirements in the respective states (CG-own and MP-own).
Capex mode (CG-own and MP-own) can yield the highest financial savings. SECL needs to explore the possibility of developing the maximum capacity of solar plant (out of 210 MW in CG and 85 MW in MP) under this mode. For this, SECL needs to initiate the following steps:
  Initiate suitability assessment of identified own lands for solar PV plant development.
  Initiate discussion with STU and Discoms for details of the nearest desired sub-stations.
  Based on the identified land parcel’s suitability study report, initiate additional land parcel procurement process at CG and MP (if required) near STU/ Discoms with available evacuation capacities.
Purchase of solar power from un-tied commissioned / under-construction solar projects under GOI-scheme (e.g. CPSU Ph-II scheme) has the lowest risk and highest ranking. For this, SECL needs to initiate the following steps:
  SECL needs to explore available un-tied commissioned / under-construction solar projects under CPSU Ph-II scheme. A list of probable such un-tied solar projects under CPSU Ph-II scheme (Tranche-III) is provided in Annexure-4.
Capacity-mix for these two options:
  Capacity under Capex mode (CG-own and MP-own) will be as per availability of suitable land as explained above.
  For remaining capacity, SECL will need to explore un-tied capacities under CPSU Ph-II scheme as explained above.

## Slide 119
Comparison of Options for Selling of Surplus Power

## Slide 120: Comparison of Various Options for Surplus Power Selling of SECL
Overall ranking based on Financial and Implementation Risks |  |  |  |  |  | 
Key Takeaways
Energy Sale to discoms is the lowest risk option followed by Energy Banking. However, the willingness and conventional practice of the discoms will play a key role in selling the surplus power sell of SECL.
Land Ownership -> | Energy Sale to Discoms | Energy Banking | Sell through Energy Exchanges | Sell through Trading Licensees | Sell to Open Access Consumers | Renewable Energy Certificate (REC)
Off-take / Volume Risk |  |  |  |  |  | 
Price Volatility Risk |  |  |  |  |  | 
Regulatory Risk |  |  |  |  |  | 
Open Access Availability Challenges |  |  |  |  |  | Absent
Multiple Consumer Management Risk |  |  |  |  |  | 
Overall Operational Complexity |  |  |  |  |  | 
Consumer Willingness |  |  |  |  |  | 

## Slide 121: Recommendations for SECL for choice of Options for Sale of Surplus Power
Three models are evaluated to be the most preferred ones:
  Sale of solar power to the discoms in Chhattisgarh and Madhya Pradesh;
  Banking of Solar Energy in Chhattisgarh and Madhya Pradesh;
  Sale of solar power to trading licensees.
Energy Sale to Discoms is the best feasible model for selling surplus power. However, CG Discom has expressed that they will not buy any solar power except from SECI. SECL can initiate communication with MP-Discoms (or MPPMCL) for the possibility to sale solar power.
SECL can start communication channel with the discoms in CG and MP for Energy Banking and necessary procedures.
SECL should start liaising with Energy Traders (such as PTC, NVVN, etc.) to find long-term contract rates and exploring the opportunity to enter into arrangements with the Traders for sale of solar power.
At the same time, SECL will also need to assess the suitability of available land parcels in CG and MP (including availability of sub-stations with spare capacities) for solar project development. SECL will need to liaise with the STU and State Discoms for assessing available evacuation capacities. For the balance land, if any, SECL will need to explore the availability of purchasing suitable land in CG and MP.

## Slide 122: Conclusion and Way Forward

## Slide 123: Way Forward for establishing solar power plant for self consumption
 | STU/ Discoms Spare Capacity Check | Deliberations need to be made with the STU and Discoms in Chhattisgarh and Madhya Pradesh to explore spare evacuation capacities at their existing and upcoming sub-stations
 | Check Availability of Own Land | Availability of own land near those identified substations need to be explored
 | Land Suitability Assessment | Suitability for development of solar power plant in those own land need to be assessed, keeping in consideration the voltage and capacity limits as per regulations for grid connectivity
 | Finding Other Private Suitable Land, if required | If availability of own land is not adequate, then availability of other lands close to the identified substations of STU and Discoms need to be explored Suitability for development of solar power plant in those land parcels need to be assessed
 | Finding Untied Solar Capacity from CPSU Scheme | Simultaneously, untied solar capacities already commissioned or about to be commissioned under the CPSU scheme Phase-II can be explored The potential for procuring those untied solar capacities can be assessed

## Slide 124: Way Forward for establishing solar power plant for sale to other parties
 | STU/ Discoms Spare Capacity Check and Land Assessment | Similar to establishing solar power plant for self-consumption, availability for spare evacuation capacities of STU and discoms sub-stations in Chhattisgarh and Madhya Pradesh alongwith availability of land (own/ others) suitable for solar power plants need to be explored
 | MP Discoms Appetite Assessment | Opportunity may be explored with MPPMCL to assess the requirement to procure solar power by MP Discoms.
 | Checking Energy Banking Steps | Deliberations to be made with discoms and regulatory commissions of CG and MP to discuss the next steps for energy banking
 | Sale to Power Traders | Deliberations may be made with the leading power traders to understand the opportunity for power sale through the traders.
 | Finding Large Open Access Consumers | Exploring potential for sell to large industrial Open Access consumers in Chhattisgarh and Madhya Pradesh as the capacity is of significantly high amount

## Slide 125: Way forward in terms of Institutional Readiness
 | Organizational Strengthening and Capacity development | Solar-specific functions like Engineering, Project management, Contract management, Commercial and Regulatory, etc. need to be developed and strengthened within SECL. The need for capacity development of SECL’s internal workforce may be envisaged in order to undertake the necessary activities for managing the solar business in a market-driven environment that involves liaison with state utilities and Regulators, handling the sale of solar energy to third-parties, power exchanges, REC-s, managing the commercial and regulatory aspects.
 | Deployment of Owner’s Engineer and Project Management Consultants | Possibility to deploy Owner’s Engineer and Project Management Consultants to obtain support in engineering, procurement, construction, commissioning and plant operations needs to be explored. A list of the names of the leading Owner’s Engineer and Project Management Consultants and EPC-cum-O&M players are provided in Annexure-5.
 | Capital cost optimization | Capital cost optimization is a major lever to achieve project financial viability. SECL needs to evaluate various avenues to optimize capital cost, which may include negotiations with OEMs / EPC players, direct procurement of major components of solar power plant instead of turnkey procurement. A structured vendor-management mechanism may be developed within SECL, wherein periodic empanelment of leading vendors/OEMs may be carried out by SECL, and database of vendors/OEMs of major components (along with their technical specs and latest prices) may be maintained through regular coordination with vendors.

## Slide 126: Summary of Recommendation and Key Steps to be Undertaken
Selection of Business Model
Capex model plant on own land is the most financially viable option with overall second rank
Amongst Capex model options, plants located in CG and MP supplying power to respective states is most financially viable option
However, this model will be successful subject to availability of suitable own land
Government Scheme e.g. CPSU Ph-II Scheme (un-tied capacity) although ranks low in financial viability but ranks highest in terms of overall attractiveness
SECL will need to explore both the above business models
Actionable Items for Capex Mode (Own Land) and GoI Scheme
Capex Mode (Own Land)
Initiate suitability assessment of identified own lands for solar PV plant development
Initiate discussion with STU and Discoms for details of nearest desired sub-stations / availability of evacuation capacity
Based on the identified land parcel’s suitability study report, initiate additional land parcel procurement process at CG and MP (if required) near STU/ Discoms with available evacuation capacities
Application for connectivity at nearby available and suitable sub-stations
GoI Scheme (CPSU Scheme Phase-II)
Un-tied solar capacities already commissioned/under-construction can be explored
Implementation Activities
SECL may consider selection of the Owner’s Engineer-cum-PMC consultant to obtain assistance for carrying out the land suitability assessment, engineering/ design, costing, procurement, project management, O&M management
Development and strengthening of solar specific function
SECL needs to evaluate various avenues to optimize capital cost, which may include negotiations with OEMs / EPC players, direct procurement of major components of solar power plant etc.
Actionable for Surplus Power Sale
Energy Sale to Discoms is the best feasible model for selling surplus. However, CG Discom has expressed that they will not buy any surplus power. SECL can initiate communication with MP-Discoms.
SECL can start communication channel with the discoms in CG and MP for Energy Banking and necessary procedures
SECL should start liaising with Energy Traders (such as PTC, NVVN, etc.) to find long-term contract rates and exploring the opportunity to enter into arrangements with the Traders for sale of solar power.
SECL will also need to assess land-suitability, evacuation infra assessment, and balance land purchase (if required) in similar lines as Capex Mode.
Self-Consumption & Plant Set-up
Surplus Power Sale

## Slide 127: Alternatives for SECL
Battery Storage
As per market standard, Battery storage capacity at the plant increases the landed cost of the Solar Energy by almost Rs. 7-8/ kwh. Apparently, the additional cost is not viable for setting up the battery storage unit under any model or any location for implementation
If the capacity of Battery Energy Storage System (BESS) is such that it can store all the surplus solar energy produced during day-time and the same fully caters SECL’s requirement during the night time, then SECL will not need to procure any further electricity from the discom. In such a case, SECL will no longer need to remain a consumer of the discom
A cost-benefit analysis need to be undertaken to compare the landed cost of solar plus BESS energy Vs discoms charge (energy Charge + fixed charge + open access charges) to assess the commercial viability of the BESS model
Open Access charges can be avoided if solar PV plant and BESS system is co-located at individual consumption points of SECL
SECL may explore the viability of Solar PV + BESS system
02
Rooftop Solar Projects
SECL is already implementing 4.38 MWp of rooftop solar project at its non-residential buildings.
SECL can further evaluate feasibility of setting up additional rooftop solar projects at available spaces.
A rooftop solar project will be financially viable only when the cost of generation from rooftop the solar project is economical compared to the applicable discom energy charge rate. Accordingly, a techno-commercial viability analysis needs to be undertaken taking into consideration the available and suitable rooftop spaces with SECL.
Such rooftop solar projects, although at much smaller capacity compared to ground-mounted solar projects, will contribute to achieving Net-Surplus status of SECL.
01
SECL may explore some additional / alternate options for the Net Surplus Strategy

## Slide 128: Annexures

## Slide 129
ANNEXURE-1: CPSU SCHEME PHASE-II

## Slide 130: CPSU Scheme Phase-II
Government of India, through Ministry of New & Renewable Energy (MNRE) has approved the implementation of CPSU Scheme Phase-II for setting up 12,000 MW grid-connected Solar Photovoltaic (PV) Power Projects by CPSUs/ State PSUs/ Government Organizations, with Viability Gap Funding (VGF) support for self-use or use by Government/ Government entities, either directly or through Distribution Companies (DISCOMS).
12000 MW Grid Connected Solar PV
“Indian Renewable Energy Development Agency Limited (IREDA) is the Implementation Agency which will allocate the VGF fund by bidding using bucket filling method”
Only for Government Producers
“a) directly controlled by the Central or State Government or
b) is under the administrative control of Central or State Government or
c) a company in which Government is having more than 50% shareholding.
For Self/ Govt. Entities’ Consumption
“a) directly controlled by the Central or State Government or
b) is under the administrative control of Central or State Government or
c) a company in which Government is having more than 50% shareholding.
Bidding by IREDA based on Viability Gap Funding (VGF)
“a) Maximum Rs. 0.55 Cr /MW, to be decided through bidding
b) VGF will be released in two tranches as follows:
i.50% on Award of contract to the EPC contractor
ii. Balance 50% on successful commissioning of the full capacity of the project
Rs. 2.45/kWh
Capping for Tariff
30 months
Commissioning Timeline

## Slide 131: History of award of solar projects under CPSU Scheme Phase-II
Tranche | Nodal Agency | Bidder's Name | Awarded Capacity (MW) | VGF (INR/MW) | Date of E-Reverse Auction | Ceiling Tariff (Rs/kWh)
I | SECI | NHDC Limited | 25 | 5500000 | 20.08.2019 | 3.50
 |  | THE SINGARENI COLLIERIES COMPANY LIMITED | 90 | 6000000 | 20.08.2019 | 3.50
 |  | ASSAM POWER DISTRIBUTION COMPANY LIMITED | 30 | 6800000 | 20.08.2019 | 3.50
 |  | DELHI METRO RAIL CORPORATION LIMITED | 3 | 6975000 | 20.08.2019 | 3.50
 |  | NALANDA UNIVERSITY | 5 | 6995555 | 20.08.2019 | 3.50
 |  | NTPC Limited | 769 | 7000000 | 20.08.2019 | 3.50
II | SECI | THE SINGARENI COLLIERIES COMPANY LIMITED | 81 | 6800000 | 08.11.2019 | 3.50
 |  | Indore Municipal Corporation | 100 | 6880000 | 08.11.2019 | 3.50
 |  | NTPC Limited | 923 | 7000000 | 08.11.2019 | 3.50
III | IREDA | SJVN Limited | 1000 | 4472000 | 23.09.2021 | 2.45
 |  | NLC India Limited | 510 | 4474990 | 23.09.2021 | 2.45
 |  | NHPC Limited | 1000 | 4490000 | 23.09.2021 | 2.45
 |  | IRCON International Limited | 500 | 4494000 | 23.09.2021 | 2.45
 |  | NTPC Limited | 1990 | 4495000 | 23.09.2021 | 2.45

## Slide 132
ANNEXURE-2: SECL’S ENERGY CONSERVATION PLAN TILL FY23

## Slide 133
SECL’s Energy Conservation Plan till FY23
Measure | Energy Saving Potential (MU)
LED Lights | 6.62
EE Fans | 3.84
EE Motors | 3.94
EE ACs | 0.76
EE Water Heaters | 0.09
Auto Timers | Not Assessed
Total | 15.24
Source: SECL

## Slide 134
ANNEXURE-3: CRITERIA FOR CAPTIVE POWER PLANT

## Slide 135: Criteria for CPP as per the Electricity Rules 2005 CPP Plants have some critical criteria and hence CPP plant needs to be segregated from the surplus sales plant
Ownership Criteria
Single Captive User- Holding of Minimum 26% Ownership of the CPP.
Group Captive User- Collective holding of minimum 26% ownership of the CPP
(“Ownership” means equity share capital with voting rights)
Energy Consumption Criteria
Single Captive User- Consumption of minimum 51% of the annual electricity generated by the CPP.
Group Captive Users (Association of Persons)-
  Collective consumption of minimum 51% of the annual electricity generated by the CPP.
  Individual Group Captive User to annually consume electricity in proportion to its shareholding with a permissible variation of +/- 10%.

## Slide 136: Criteria for CPP as per the Electricity Rules 2005 (1/2) 1. Ownership Criteria
Provisions as per the Electricity Rules 2005
Single Captive User- Holding of Minimum 26% Ownership of the CPP.
Group Captive User- Collective holding of minimum 26% ownership of the CPP.
(“Ownership” means equity share capital with voting rights)
Rule 3. Requirements of Captive Generating Plant.- | 
Rule | Statement
Rule 3(1) | No power plant shall qualify as a ‘captive generating plant’ under section 9 read with clause (8) of section 2 of the Act unless-
 | (a) in case of a power plant - not less than twenty six percent of the ownership is held by the captive user(s), and not less than fifty one percent of the aggregate electricity generated in such plant, determined on an annual basis, is consumed for the captive use: Provided that in case of power plant set up by registered cooperative society, the conditions mentioned under paragraphs at (i) and (ii) above shall be satisfied collectively by the members of the co-operative society. Provided further that in case of association of persons, the captive user(s) shall hold not less than twenty six percent of the ownership of the plant in aggregate and such captive user(s) shall consume not less than fifty one percent of the electricity generated, determined on an annual basis, in proportion to their shares in ownership of the power plant within a variation not exceeding ten percent.

## Slide 137: Criteria for CPP as per the Electricity Rules 2005 (2/2) 2. Electricity Consumption Criteria
Provisions as per the Electricity Rules 2005
Single Captive User- Consumption of minimum 51% of the annual electricity generated by the CPP.
Group Captive Users (Association of Persons)-
  Collective consumption of minimum 51% of the annual electricity generated by the CPP.
  Individual Group Captive User to annually consume electricity in proportion to its shareholding with a permissible variation of +/- 10%.
Rule 3. Requirements of Captive Generating Plant.- | 
Rule | Statement
Rule 3(1) | No power plant shall qualify as a ‘captive generating plant’ under section 9 read with clause (8) of section 2 of the Act unless-
 | (a) in case of a power plant - not less than twenty six percent of the ownership is held by the captive user(s), and not less than fifty one percent of the aggregate electricity generated in such plant, determined on an annual basis, is consumed for the captive use: Provided that in case of power plant set up by registered cooperative society, the conditions mentioned under paragraphs at (i) and (ii) above shall be satisfied collectively by the members of the co-operative society. Provided further that in case of association of persons, the captive user(s) shall hold not less than twenty six percent of the ownership of the plant in aggregate and such captive user(s) shall consume not less than fifty one percent of the electricity generated, determined on an annual basis, in proportion to their shares in ownership of the power plant within a variation not exceeding ten percent.

## Slide 138
ANNEXURE-4: POSSIBLE UN-TIED CAPACITIES AWARDED UNDER CPSU SCHEME PHASE-II TRANCHE-III

## Slide 139: Status of tie-up of Solar Projects awarded under CPSU Scheme Ph-II Tranche-III, and probable un-tied capacities
Tranche | Nodal Agency | Name of Successful Bidder | Awarded Capacity (MW) | Ceiling Tariff (Rs/kWh) | Tie-up Status
III | IREDA | SJVN Limited | 1000 | 2.45 | Plant to be set up in Bikaner, Rajasthan; EPC contract awarded to Tata Power Solar in May 2022; Tie up with NDMC for sale of 150 MW power @Rs. 2.44/kWh; Balance capacity that can be explored by SECL: 850 MW
 |  | NLC India Limited | 510 | 2.45 | 
 |  | NHPC Limited | 1000 | 2.45 | Plant to be set up in Gujarat (600 MW), Rajasthan (300 MW) and Andhra Pradesh (100 MW); EPC contract awarded to Adani Infra, Tata Power Solar, and SSEL-ASR JV in May 2022; PUA with Telangana Discoms under process for 500 MW @Rs. 2.45/kWh; Balance capacity that can be explored by SECL: 500 MW
 |  | IRCON International Limited | 500 | 2.45 | Plant to be set up at Pavagada, Karnataka; PPA for entire capacity signed with South Western Railway in May 2022
 |  | NTPC Limited | 1990 | 2.45 | Plant to be set up at Nokh Solar Park, Rajasthan and Khavda Solar PV Station, Gujarat; PUA signed with Telangana Discoms in Dec 2021 for 1045 MW; 100 MW PUA with DVC Balance capacity that can be explored by SECL: 845 MW

## Slide 140
ANNEXURE-5: LIST OF LEADING EPC-CUM-O&M PLAYERS AND OWNER’S ENGINEER-CUM-PMC PLAYERS

## Slide 141: Details of Leading EPC-cum-O&M Players
Sl. No | Name of the Player | Name of the Key Person | Contact No | Email ID
1 | McNally Bharat Engineering Company Limited | Babula Purnachandra Muni | +918249601030 | Babula.muni@mbecl.co.in
2 | Pennar Industries Limited | N. Dayasagar Rao | +919848757755 | Dayasagar.neelagiri@pennarindia.com
3 | Hild Energy Private Limited | K.R.M. Prakash Kumar | +919176628359 | prakash@hildenergy.com
4 | Waree Energies Limited | Sunil Rathi | +918291931002 | tender@waree.com
5 | Vikram Solar Limited | Praveen Kumar Jha | +919830811197 | praveen.jha@vikramsolar.com
6 | KEC International Limited | Anupam Gupta | +919871371628 | guptaanupam@kecrpg.com
7 | Larsen & Toubro Limited | Shaji John | +919444962878 | sjn@lntecc.com
8 | Sterling and Wilson Solar Limited | Rahul Kshetrapal | +919999712733 | Rahul.kshetrapal@sterlingwilson.com
9 | Sukhbir Agro Energy Limited | Amit Antil | +919958949594 | Amit.antil@sael.co
10 | Tata Power Solar Systems Ltd | Mintu Roy | +918097141264 | Mintu.roy@tatapowersolar.com
11 | Mytrah Energy (India) Private Limited | Debasish Das | +919560872323 | Debasish.das@mytrah.com
12 | Rays Power Infra Private Limited | Abhishek Swarnakar | +917290035777 | Abhishek.swarnakar@rayspowerinfra.com
13 | Bharat Heavy Electricals Limited | Mani Bhushan Sharma | +919716913941 | manisharma@bhel.in
14 | Adani Infra (India) Ltd | Dhaivat Joshi | +919099900955 | Solar.bd@adani.com
15 | Refex Energy Limited | SK Lokesh | +918019018719 | Lokesh.s@refexenergy.com
16 | Jackson Limited | Rajesh Singh |  | Rajesh.singh@jackson.com
17 | Amara Raja Power Systems Ltd. |  |  | bsd@amararaja.com
18 | BVG India Ltd | Pankaj Dhingra |  | Pankaj.Dhingra@bvgindia.com

## Slide 142: Details of Leading Owner’s Engineer-cum-PMC Players
Sl. No | Name of the Player | Name of the Key Person | Contact No | Email ID
1 | ABPS Infrastructure Advisory Pvt Ltd | Vinod Kumar Gambhir | +919599556529 | Vinod.gambhir@abpsiapl.com
2 | Canyon Consultancy Private Limited | Surajit Jenamani | +919778203273 | info@canyonconsultancy.com
3 | AHAsolar Private Limited | Vipin Sharma | +919725276862 | vipin.s@ahasolar.in
4 | Gujarat Energy Research & Management Institute | Kaushik Patel | +917923275757 | Kausik.p@germi.res.in
5 | TUV SUD South Asia Pvt Ltd | Piyush Sharma | +917208955845 | piyush.sharma@tuvsud.com
6 | L&T-Sargent & Lundy Ltd | Amit Kumar Pal | +919555575573 | Amitkumar.pal@lntsnl.com
7 | AECOM India Pvt Ltd | Sanket Menjoge | +91124 4830100 | Sanket.menjoge@aecom.com
8 | Dornier Group (India) Private limited | Anup Bhargava | +91 124 4080320 | anup.bhargava@dorniergroup.com
9 | Tractebel Engineering Private Limited | Chiranmay Sarkar | +919999432567 | chiranmay.sarkar@tractebel.engie.com
10 | RINA Consulting Pvt Ltd | Naveen Kumar | +9122 6111 3333 | Swapnil.nayak@rina.org
11 | TruBoard Credit Monitoring Services Private Limited | Tilkesh Purohit | +919820407680 | contact@truboardpartners.com
12 | Power and Energy Consultants India Private Ltd | Chandra Mohan Jain | +911142171115 | info@powerandenergyconsultants.com
13 | TUV Rheinland India Pvt Ltd | Anil Kumar Goud | +91953 88 66 444 | anil.goud@ind.tuv.com
14 | MITCON Consultancy and Engineering Services Ltd. | Ganesh Salunke | +918669661689 | ganesh.salunke@mitconindia.com
15 | Ayesa India Private Limited | Pushpendra Kumar Gupta | +919582294442 | pkgupta@ayesa.com
16 | Fichtner Consulting Engineers (India) Private Limited | R. Venkata Ramana | +919445021840 | Venkataramana_r@fichtnerindia.com
17 | Infrastructure Development Corporation (Karnataka) Ltd. | T. Paul Koshy | +91 80 43448000 | bd@ideck.in
18 | SMEC (India) Pvt. Ltd. | Mallikarjungowda Patil | +91 9000106767 | m.patil@smec.com
19 | Archer Business Solution Pvt Lys | Devender Singh Rawat | +919910053877 | contact@archerbisuness.in
20 | TUV India Private Limited | Ravindran R | +919940622942 | rravindran@tuv-nord.com

## Slide 143
ANNEXURE-6: LANDED COST OF SOLAR ENERGY FOR BOO-MODE AND GOI SCHEME-MODE

## Slide 144: Landed Cost of Solar Energy under BOO-mode (Rs/kWh)
For Option 1: Full Capacity in CG and Consumption in both CG and MP
Particulars |  | Scenarios of BOO Solar Tariff at Generation-end (constant BOO tariff for 25 years) (Rs/kWh) |  |  |  | 
 |  | 2.20 | 2.50 | 3.00 | 3.50 | 4.00
Landed cost of solar generation in CG | Year-1 | 2.45 | 2.77 | 3.30 | 3.84 | 4.37
 | Year-25 | 2.45 | 2.77 | 3.30 | 3.84 | 4.37
Landed cost of solar generation in MP (without ISTS-waiver) | Year-1 | 12.15 | 12.53 | 13.15 | 13.78 | 14.40
 | Year-25 | 23.49 | 23.86 | 24.48 | 25.11 | 25.73
Landed cost of solar generation in MP (with ISTS-waiver) | Year-1 | 8.20 | 8.58 | 9.20 | 9.82 | 10.45
 | Year-25 | 14.63 | 15.00 | 15.63 | 16.25 | 16.88

## Slide 145: Landed Cost of Solar Energy under BOO-mode (Rs/kWh)
For Option 2: Full Capacity in MP and Consumption in both CG and MP
Particulars |  | Scenarios of BOO Solar Tariff at Generation-end (constant BOO tariff for 25 years) (Rs/kWh) |  |  |  | 
 |  | 2.20 | 2.50 | 3.00 | 3.50 | 4.00
Landed cost of solar generation in CG (without ISTS-waiver) | Year-1 | 10.35 | 10.73 | 11.35 | 11.97 | 12.60
 | Year-25 | 18.54 | 18.92 | 19.54 | 20.16 | 20.79
Landed cost of solar generation in CG (with ISTS-waiver) | Year-1 | 6.42 | 6.79 | 7.42 | 8.04 | 8.67
 | Year-25 | 9.73 | 10.10 | 10.73 | 11.35 | 11.98
Landed cost of solar generation in MP | Year-1 | 7.00 | 7.33 | 7.88 | 8.43 | 9.07
 | Year-25 | 13.05 | 13.38 | 13.93 | 14.48 | 15.03

## Slide 146: Landed Cost of Solar Energy under BOO-mode (Rs/kWh)
For Option 3: CG demand met by capacity in CG, MP demand met by capacity in MP
Particulars |  | Scenarios of BOO Solar Tariff at Generation-end (constant BOO tariff for 25 years) (Rs/kWh) |  |  |  | 
 |  | 2.20 | 2.50 | 3.00 | 3.50 | 4.00
Landed cost of solar generation in CG | Year-1 | 2.45 | 2.77 | 3.30 | 3.84 | 4.37
 | Year-25 | 2.45 | 2.77 | 3.30 | 3.84 | 4.37
Landed cost of solar generation in MP | Year-1 | 7.00 | 7.33 | 7.88 | 8.43 | 8.98
 | Year-25 | 13.05 | 13.38 | 13.93 | 14.48 | 15.03

## Slide 147: Landed Cost of Solar Energy under GOI Scheme (Rs/kWh)
For Option 3: CG demand met by capacity in CG, MP demand met by capacity in MP (Options 1 & 2 are not relevant in this case)
Particulars |  | Scenarios of BOO Solar Tariff at Generation-end (constant BOO tariff for 25 years) (Rs/kWh) |  |  |  | 
 |  | 2.20 | 2.50 | 3.00 | 3.50 | 4.00
Landed cost of solar generation in CG (without ISTS-waiver) | Year-1 | 8.12 | 8.44 | 8.97 | 9.50 | 10.04
 | Year-25 | 12.97 | 13.29 | 13.82 | 14.36 | 14.89
Landed cost of solar generation in CG (with ISTS-waiver) | Year-1 | 4.43 | 4.75 | 5.28 | 5.81 | 6.34
 | Year-25 | 4.70 | 5.02 | 5.55 | 6.09 | 6.62
Landed cost of solar generation in MP (without ISTS-waiver) | Year-1 | 10.82 | 11.15 | 11.71 | 12.26 | 12.81
 | Year-25 | 21.62 | 21.95 | 22.50 | 23.05 | 23.60
Landed cost of solar generation in MP (with ISTS-waiver) | Year-1 | 7.00 | 7.33 | 7.88 | 8.43 | 8.98
 | Year-25 | 13.05 | 13.38 | 13.93 | 14.48 | 15.03

## Slide 148
Deloitte refers to one or more of Deloitte Touche Tohmatsu Limited, a UK private company limited by guarantee (“DTTL”), its network of member firms, and their related entities. DTTL and each of its member firms are legally separate and independent entities. DTTL (also referred to as “Deloitte Global”) does not provide services to clients. Please see www.deloitte.com/about for a more detailed description of DTTL and its member firms.
This material has been prepared by Deloitte Touche Tohmatsu India LLP (“DTTILLP”), a member of Deloitte Touche Tohmatsu Limited, on a specific request from you and contains proprietary and confidential information. This material may contain information sourced from publicly available information or other third party sources. DTTILLP does not independently verify any such sources and is not responsible for any loss whatsoever caused due to reliance placed on information sourced from such sources. The information contained in this material is intended solely for you. Any disclosure, copying or further distribution of this material or its contents is strictly prohibited.
Nothing in this material creates any contractual relationship between DTTILLP and you. Any mutually binding legal obligations or rights may only be created between you and DTTILLP upon execution of a legally binding contract. By using this material and any information contained in it, the user accepts this entire notice and terms of use.
©2022 Deloitte Touche Tohmatsu India LLP. Member of Deloitte Touche Tohmatsu Limited
Deloitte Touche Tohmatsu India Private Limited (U74140MH199 5PTC093339), a private company limited by shares, was converted into Deloitte Touche Tohmatsu India LLP, a limited liability partnership (LLP Identification No. AAE-8458),with effect from October 1, 2015.