## Cover Page
Bakreswar FSPV Financial Model- DPR

## RA
PVSyst File | [10 empty] | SolarGIS
| GlobHor | DiffHor | T_Amb | GlobInc | GlobEff | EArray | E_Grid
| kWh/m² | kWh/m² | °C | kWh/m² | kWh/m² | MWh | MWh | PR | Capacity (MW) | Days | CUF
January | 121.6 | 63.7 | 17.1 | 129.4 | 120.5 | 26234 | 24195 | 0.767 | 180.418 | 31 | 18.02%
February | 137.5 | 61.8 | 21 | 144.6 | 135.4 | 29173 | 28629 | 0.812 | 180.418 | 28 | 23.61%
March | 182.8 | 77.6 | 26.1 | 188.7 | 177.3 | 37507 | 36770 | 0.799 | 180.418 | 31 | 27.39%
April | 189.6 | 87.2 | 29.9 | 191.9 | 180.4 | 37626 | 36889 | 0.788 | 180.418 | 30 | 28.4%
May | 182.3 | 101.1 | 30.7 | 181.9 | 170.6 | 35441 | 34791 | 0.784 | 180.418 | 31 | 25.92%
June | 150.3 | 95.4 | 30.3 | 149 | 139.3 | 28999 | 28494 | 0.784 | 180.418 | 30 | 21.94%
July | 139.5 | 91.3 | 29.1 | 138.7 | 129.6 | 27101 | 26626 | 0.787 | 180.418 | 31 | 19.84%
August | 143.4 | 89.7 | 29 | 143.9 | 134.6 | 28175 | 27673 | 0.789 | 180.418 | 31 | 20.62%
September | 135.7 | 80.1 | 28.5 | 137.9 | 129.1 | 27085 | 26592 | 0.79 | 180.418 | 30 | 20.47%
October | 143.3 | 73.6 | 26.9 | 148.8 | 139.1 | 29351 | 28821 | 0.794 | 180.418 | 31 | 21.47%
November | 124.3 | 64.9 | 22.8 | 131.5 | 122.8 | 26247 | 22840 | 0.712 | 180.418 | 30 | 17.58%
December | 111.2 | 62.5 | 18.49 | 118.3 | 110.1 | 23819 | 21441 | 0.743 | 180.418 | 31 | 15.97%
Year | 1761.5 | 948.9 | 25.84 | 1804.6 | 1688.8 | 356758 | 343761 | 0.781 | 180.418 | 365 | 21.75%
Option 2
| GlobHor | DiffHor | T_Amb | GlobInc | GlobEff | EArray | E_Grid
| kWh/m² | kWh/m² | °C | kWh/m² | kWh/m² | MWh | MWh | PR | Capacity (MW) | Days | CUF
January | 121.6 | 63.7 | 17.1 | 129.4 | 120.5 | 26662 | 25367 | 0.804 | 199.6 | 31 | 17.08%
February | 137.5 | 61.8 | 21 | 144.6 | 135.4 | 29646 | 29198 | 0.828 | 199.6 | 28 | 21.77%
March | 182.8 | 77.6 | 26.1 | 188.7 | 177.3 | 38108 | 37512 | 0.815 | 199.6 | 31 | 25.26%
April | 189.6 | 87.2 | 29.9 | 191.9 | 180.4 | 38230 | 37634 | 0.804 | 199.6 | 30 | 26.19%
May | 182.3 | 101.1 | 30.7 | 181.9 | 170.6 | 36021 | 35482 | 0.8 | 199.6 | 31 | 23.89%
June | 150.3 | 95.4 | 30.3 | 149 | 139.3 | 29471 | 29042 | 0.799 | 199.6 | 30 | 20.21%
July | 139.5 | 91.3 | 29.1 | 138.7 | 129.6 | 27533 | 26983 | 0.798 | 199.6 | 31 | 18.17%
August | 143.4 | 89.7 | 29 | 143.9 | 134.6 | 28631 | 28209 | 0.804 | 199.6 | 31 | 19%
September | 135.7 | 80.1 | 28.5 | 137.9 | 129.1 | 27520 | 27107 | 0.806 | 199.6 | 30 | 18.86%
October | 143.3 | 73.6 | 26.9 | 148.8 | 139.1 | 29829 | 29384 | 0.81 | 199.6 | 31 | 19.79%
November | 124.3 | 64.9 | 22.8 | 131.5 | 122.8 | 26672 | 25980 | 0.81 | 199.6 | 30 | 18.08%
December | 111.2 | 62.5 | 18.49 | 118.3 | 110.1 | 24207 | 23859 | 0.827 | 199.6 | 31 | 16.07%
Year | 1761.5 | 948.9 | 25.84 | 1804.6 | 1688.8 | 362529 | 355757 | 0.808 | 199.6 | 365 | 20.35%
Option 2
| GlobHor | DiffHor | T_Amb | GlobInc | GlobEff | EArray | E_Grid
| kWh/m² | kWh/m² | °C | kWh/m² | kWh/m² | MWh | MWh | PR | Capacity (MW) | Days | CUF
January | 121.6 | 63.7 | 17.1 | 129.4 | 120.5 | 26234 | 24204 | 0.767 | 203.24 | 31 | 16.01%
February | 137.5 | 61.8 | 21 | 144.6 | 135.4 | 29173 | 28645 | 0.812 | 203.24 | 28 | 20.97%
March | 182.8 | 77.6 | 26.1 | 188.7 | 177.3 | 37507 | 36795 | 0.8 | 203.24 | 31 | 24.33%
April | 189.6 | 87.2 | 29.9 | 191.9 | 180.4 | 37648 | 36935 | 0.789 | 203.24 | 30 | 23.8%
May | 182.3 | 101.1 | 30.7 | 181.9 | 170.6 | 35463 | 34831 | 0.785 | 203.24 | 31 | 18.85%
June | 150.3 | 95.4 | 30.3 | 149 | 139.3 | 28999 | 28505 | 0.784 | 203.24 | 30 | 18.2%
July | 139.5 | 91.3 | 29.1 | 138.7 | 129.6 | 27106 | 26636 | 0.787 | 203.24 | 31 | 18.28%
August | 143.4 | 89.7 | 29 | 143.9 | 134.6 | 28175 | 27638 | 0.789 | 203.24 | 31 | 17.6%
September | 135.7 | 80.1 | 28.5 | 137.9 | 129.1 | 27095 | 26614 | 0.791 | 203.24 | 30 | 18.19%
October | 143.3 | 73.6 | 26.9 | 148.8 | 139.1 | 29351 | 28838 | 0.795 | 203.24 | 31 | 19.07%
November | 124.3 | 64.9 | 22.8 | 131.5 | 122.8 | 26247 | 22846 | 0.712 | 203.24 | 30 | 15.61%
December | 111.2 | 62.5 | 18.49 | 118.3 | 110.1 | 23819 | 21444 | 0.743 | 203.24 | 31 | 14.18%
Year | 1761.5 | 948.9 | 25.84 | 1804.6 | 1688.8 | 356817 | 343931 | 0.808 | 203.24 | 365 | 19.32%

## Input
Circularity
|  | Units | Rate | Quantity |  |  | Levelized Tariff (Rs/ kWh) | 5.2536 |  | TRUE | TRUE
| Technical | [5 empty] | FIRR | 8.796%
| DC Capacity | MWp |  | 243.888 |  |  | EIRR | 19.49% |  | Option 2
| Conversion Factor |  |  | 1.2 | Option 2 |  | WACC | 7.476% |  | 705 | 25% Overloading
| AC Capacity - Project | MW |  | 203.24 |  |  | Rs.Crore/MW | 6.1138
| CUF of the project | % |  | 19.32% |  |  | Rs.Crore/MWp | 5.0948
| If Transmission Cost Included | # |  | Yes
| Water Depth- 73.5m | # |  | Yes |  | Senstivity | Change
|  |  | Island 1 | Island 2 |  | Project Cost | 0%
| Island unit capacity - DC | MWp | 6.087 | 4.092 |  | CUF | 0%
| Island unit capacity - AC | MW | 5.0725 | 3.41 |  | Interest Rate | 0%
| Module Size | Wp | 580 | 580 |  | Overloading Factor | 1.2
| Inverter size | MW | 4.4 | 1.1
| No of islands | # | 32 | 12
| No of Inverters | # | 44 | 12 |  |  | Overloading
| No of Inverters per island | # | 1 | 1 |  | Option 1 | 1.352
| No of modules per string | # | 28 | 28 |  | Option 2 | 1.2
| Total Modules per island | # | 336544 | 84841
| No of Module Floats per Sub Plot | # | 10496 | 7056
| No of modules per island | # | 335872 | 84672
| Spare Modules | % | 0.2% | 0.2%
| Spare Modules | # | 672 | 169
| No of Main walkway Floats per Island | # | 1180 | 856
| No of Long Secondary Float per Island | # | 4092 | 2697
| No of Short Secondary Float per Island | # | 3712 | 2436
| No of Secondary Walkway per Island | # | 597 | 416
| No of Cable Float-DC | # | 20695 | 7761
| No of Cable Float-AC | # | 24803 | 9301
| Rigid Mooring Line | KM | 68.32 | 19.32
| Flexible Mooring Line | KM | 55.36 | 15.48
| Inverter Barge- Mooring Line | KM | 5.94 | 5.94
BOQ Assumptions |  |  | Unit Rate | No of Units
A | PV System
| PV Module | # | 15.84 | 421385 | 0%
| EL Testing | # | 1000000 | 1
| Thermography | # | 500000 | 1
| Inverter 4.4 MW | # | 5700000 | 44
| Inverter 1.1 MW | # | 1187500 | 12
| Solar Project |  |  |  |  | For 73.5 m | For 72.5 m
| Float Devices |  | Rate | Quantity | As per Design
| Floats - Panel Platform | # | 1045 | 420544 | As per Design | 420544 | 349051.52
| Floats - Main walkway | # | 4018.5 | 48032 | As per Design | 48032 | 39866.56
| Floats-Long Secondary | # | 2411.1 | 163308 | As per Design | 163308 | 135545.64
| Floats- Short Secondary | # | 1607.4 | 148016 | As per Design | 148016 | 122853.28
| Floats- Secondary Walkway | # | 7968.125 | 24096 | As per Design | 24096 | 19999.68
| No of Cable Float-DC | # | 126.35 | 755372 | As per Design | 755372 | 626958.76
| No of Cable Float-AC | # | 105.45 | 905308 | As per Design | 905308 | 751405.64
| Mooring Line |  | Cost | Unit
| Mooring Line - Rigid | Rs per KM | 5878028.1 | 87.64 |  | 87.64 | 72.7412
| Mooring Line - Flexible | Rs per KM | 5878028.1 | 70.84 |  | 70.84 | 58.7972
| Mooring Accessories | Rs per unit | 7505 | 2400 |  | 2400 | 1992
| Inverter Barge | Rs. Per KM | 1055716.285 | 11.88 |  | 11.88 | 9.8604
Anchors
| Anchor Type - Gravity | Rs per Anchor | 17307.1 | 5536 |  | 5536 | 4594.88
Inverter-Transformer Platform
| Transformer of Size 5.5 MVA | Rs per unit | 5790250 | 12 | 15% erection included
| Transformer of Size 6.5 MVA | Rs per unit | 6992000 | 32 | 15% erection included
| Ferrocement Platform | Lum Sum Cost | 5500000 | 52 |  | 52 | 38
Service Cost/Installation Cost
| Panel Platform - Floats | % of Hard cost | 15%
| Floats- Main Walkways | % of Hard cost | 15%
| Floats-Long Secondary | % of Hard cost | 15%
| Floats- Short Secondary | % of Hard cost | 15%
| Floats- Secondary Walkways | % of Hard cost | 15%
| Floats- Cables | % of Hard cost | 15%
| Mooring | % of Hard cost | 15%
| Anchoring | % of Hard cost | 15%
III | General
A | Land Area |  |  | Area (Acre) | Av Length (m) | Av Width (m)
1 | 220/33 kV Sub Station | Rs Lakh/ acre | 0 | 10.125 | 225 | 180
2 | Sub station Control Room | Rs Lakh/ acre | 0 | 1 | 80 | 50
3 | Approach Road | Rs Lakh/ acre | 0 | 0.6125 | 700 | 3.5
4 | Master Control Room - FSPV | Rs Lakh/ acre | 0 | 3.8955 | 147 | 106
5 | Storage Space | Rs Lakh/ acre | 0 | 4.125 | 165 | 100
| Total Land Area |  |  | 19.758
B | Site Development
| Site Development | Rs Lakh per Acre | 100 | 15.0205
C | Road Infrastructure
1 | Access Roads | Rs Lakh per kM | 120 | 0.6125
D | Building and Civil Infrastructure
1 | Master Control Room - FSPV | Rs per sq m | 676 | 15582
2 | Offices | Rs per sq m | 676 | 20000
3 | Housing | Rs per sq m | 0 | 0
4 | Common Infrastructure | Rs per sq m | 676 | 10000
5 | Medical facilities | Rs per sq m | 0 | 0
E | Other Infrastructure
1 | Lighting | Rs per Unit | 3000 | 2000
| Security | Rs per Unit | 5000 | 400
3 | Drainage System | Rs per kM | 0 | 0
4 | Fencing | Rs per kM | 0 | 0
5 | Gates | Rs per m | 0 | 0
7 | Waste disposal and liquid sewage treatment plant | Rs per unit | 0 | 0
8 | Solid waste collection, recycling and storage | Rs per sq m | 0 | 0
9 | Cost of Green Belt | Rs per sq m | 0 | 0
10 | Any other envisaged | Rs Lakh per Unit | 0 | 0
F | Other Infrastructure
| Enviromental Mitigation Charges | Rs Lakh |  | 1000
G | Other Charges
1 | Local Area Development Charges | Rs per MW | 100000 | 203.24
2 | Registration Cost | Rs per MW | 0 | 203.24
3 | Legal Charges | Rs per MW | 0 | 203.24
4 | Regulatory Charges |  | 500000 | 1
5 | Technical Design |  | 0 | 1
| Contingency |  | 3%
Environmental Mitigation Charges
II | Evacuation Infrastructure
A | Transmission Line - General
| From |  | Pooling S/S
| To |  | BkTPS S/S
| Proposed Transmission Line Route Length for 220 kV Line | km | 4
| 220 kV Transmission Line - Configuration |  | Double Circuit-Double Strung Line
| Conductor Type |  | Single ACCC conductor Zebra Equivalent
| Average Span for 220 kV Tower | meter | 300
B | Transmission Line - 220kV Towers
1 | 220 kV Tower configuration
| Type A - Suspension Tower - 00 to 20 | % | 50% | 7
| Type B - Double Suspension Tower- 20 to 150 | % | 15% | 2
| Type C - Tension Tower - 150 to 300 | % | 10% | 1
| Type D - Dead End Tower - 300 to 600 | % | 25% | 4
2 | Weight of Towers
a | Escalation in weight of Tower for next category Tower | % | 20%
b | Type A - Suspension Tower - 00 to 20 | MT |  | 7.8
c | Type B - Double Suspension Tower- 20 to 150 | MT |  | 9.36
d | Type C - Tension Tower - 150 to 300 | MT |  | 11.232
e | Type D - Dead End Tower - 300 to 600 | MT |  | 13.4784
3 | Tower Foundations
a | Escalation in Foundation cost for next angel Tower | % | 15%
b | Type A - Suspension Tower - 00 to 20 | Rs |  | 800000
c | Type B - Double Suspension Tower- 20 to 150 |  |  | 920000
d | Type C - Tension Tower - 150 to 300 |  |  | 1058000
e | Type D - Dead End Tower - 300 to 600 |  |  | 1216700
4 | 220 kV Insulator String Numbers per pole per Tower type
a | Type A - Suspension Tower - 00 to 20 | # | 6
b | Type B - Double Suspension Tower- 20 to 150 | # | 12
c | Type C - Tension Tower - 150 to 300 | # | 18
d | Type D - Dead End Tower - 300 to 600 | # | 30
C | Transmission Line - 220kV Conductors
| Conductor Configuration |  | Single ACCC conductor Zebra Equivalent
| Extra Conductor length for sagging & wastage | % | 5%
| Maximum length of ACCC Conductor Zebra Equivalent | meter per drum | 900
| Repairing Sleeve suitable for ACCC Zebra Conductor Equivalent for minium stretch length | km | 2
D | 33/220 KV - 300 MW Pooling Sub-Station
1 | 33/220 kV, 80 MVA Power Transformer | # | 4
2 | 33kV Incomer Feeder Bays (25MW) to 33 kV Bus | # | 12
3 | 33 kV Bus Section & Bus Coupler Bays | # | 8
4 | 33kV incoming feeders for Power transformer | # | 4
5 | Reactive Power Compensation as per CEA connectivity standard, | MVAr | 60
6 | 220kV Power Transformer Bay | # | 4
7 | 220 kV Line Bay+ Bus Coupler Bay | # | 3
8 | 220 kV Bus Transfer Bay | # | 1
9 | Control & Communication | # | 1
E | Augmentation Work @ BkTPS Substation
1 | 220 kV Line Bay+ Bus Section Bay | No. | 2
2 | EHV Cabling | Mtr | 300
3 | Miscelaneous ( Control and Protection) | No. | 1
F | Evacuation System - Other Costs
|  |  | Sub-station | Transmission Liine | Augmentation
| GST | % | 18% | 18% | 18%
| Erection, testing, commissioning charges | % | 20% | NA | 20%
| Transport Charges | % | 5% | NA | 5%
| Insurance and Labour | % | 2% | NA | 2%
| Centage charges | % of hard cost | NA | 5% | NA
| Labour & Equipment Handling charges | % of hard cost | 8% | 8% | 8%
| Supervision & Quality Control Charges | % of hard cost | 5% | 5% | 5%
| Net |  | 13% | 13% | 13%
C | Project Details
| Start of Project |  |  | 2025-04-01
| Construction Period | Months |  | 18
| Start of Operation | Date |  | 2026-10-01
| Number of year in operation | Years |  | 25
| First operational Financial year | Date |  | 2027-03-31
| Last day of operation | Date |  | 2051-09-30
| Last financial year of operation | Date |  | 2052-03-31
Commercial Loan 1
| Moratorium Period (from start of operations) | Years |  | 0
| Repayment Period | Years |  | 15 | As per ADBs Input
| Interest Rate | % |  | 6% | As per ADBs Input
Commercial Loan 2
| Moratorium Period (from start of operations) | Years |  | 0
| Repayment Period | Years |  | 15
| Interest Rates | % |  | 8.5%
Equity
| Return on Equity (RoE) - Post Tax | % |  | 14% | As per CERC Notification dated 12th June 2024
| DSRA Months | months |  | 0
| DSRA Source |  |  | BG
| Bank Guarantee Fee | % |  | 0%
| Interest on DSRA | % |  | 4%
Cash Deficit Loan
| Interest Rates on Cash Deficit Loan | % |  | 9%
| Repayment of Cash Deficit Loan |  |  | TRUE
| Minimum Cash Balance | Rs Cr |  | 0
O&M - Generation
| O&M per MW (excld GST) | Rs Lakh/MW |  | 4.66
| O&M per MW (incld GST) | Rs Lakh/MW |  | 5.4988 | As provided by WBPDCL
| O&M Escalation | % |  | 5.25% | As per CERC Notification dated 12th June 2024
O&M - Infrastructure
| Lease Rent | Rs Lakh/ MW |  | 0 | 5%
| Water Use charges | Rs Lakh/ Litre |  | 0 | 5%
| Road, building maintenance | % of Assets |  | 1%
| SLDC Charges | Rs Lakh/ MW |  | 0 | 5% |  |  |  |  | State Regulations
| A&G Charges | Rs Lakh/ MW |  | 0 | 3.7% |  |  |  |  | Bakreswar | Nos # | O&M (Rs L) | Annual O&M Norms | FY 23 | FY 24
| Transmission O&M Charges | Rs Lakh/ MW |  | 1.194 | [5 empty] | Sub-station bays | 8 | 206.72 | 220 kV Sub-station (Rs Lakh/ bay) | 24.96 | 25.84
| O&M Escalation | % |  | 3.77% | [5 empty] | Transformer (MVA) | 300 | 84.6 | 220 kV Transformer (Rs L/MVA) | 0.272 | 0.282
Working Capital | [9 empty] | Net | 1.1945 | 291.32 | O&M Escalation | 4.02%
| Receivables | Months |  | 1.5 | (Sector Norms) | As per 4.13.2 of https://wberc.gov.in/sites/default/files/TP%20103-1.pdf
| O&M | Months |  | 1 | (Sector Norms) | As per 4.13.2 of https://wberc.gov.in/sites/default/files/TP%20103-1.pdf
| Maintenance spares | % |  | 15%
| Interest on WC | % |  | 11.5%
| Margin Money for WC | % |  | 25%
Others |  |  |  |  | Supply | Services
| Tax Rate | % |  | 22% | As provided by WBPDCL
| MAT Rate | % |  | 17.16%
| GST | % |  | 18% | 12% | 18% | 13.8%
| IRG to be considered | % |  | FALSE
| Dismantling Cost (% of GFA) | % |  | 0.25%
| Discounting Factor | % |  | 7.476%
Solar Park
| Infrastructure Cost part of Generation Tariff | Yes |  | TRUE
Tariff
| Tariff Options (TRUE: Levelized; FALSE: Yearly Tariff) |  |  | TRUE
| Levelized Tariff |  |  | 5.2536
Yearly Assumptions for generation model
| Particulars | Units | Inputs | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057
|  |  | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31 | 2031-03-31 | 2032-03-31 | 2033-03-31 | 2034-03-31 | 2035-03-31 | 2036-03-31 | 2037-03-31 | 2038-03-31 | 2039-03-31 | 2040-03-31 | 2041-03-31 | 2042-03-31 | 2043-03-31 | 2044-03-31 | 2045-03-31 | 2046-03-31 | 2047-03-31 | 2048-03-31 | 2049-03-31 | 2050-03-31 | 2051-03-31 | 2052-03-31 | 2053-03-31 | 2054-03-31 | 2055-03-31 | 2056-03-31 | 2057-03-31
| Capacity Degradation | % |  | 0% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
| APC | % |  |  | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75%
| Generation and Transmission | % |  | 51.65% | 48.35% | bar: 2028-03-31 to 2057-03-31
| Civil and Other Infastructure | % |  | 30% | 70% | bar: 2028-03-31 to 2057-03-31
| Other Cost | % |  | 10% | 90% | bar: 2028-03-31 to 2057-03-31
Funding
| Commerical Loan 1 | % |  | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70%
| Commerical Loan 2 | % |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grant/ Capital Subsidy | % |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equity | % |  | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30%
Depreciation
| Rate of Depreciation (Book) | % | 15 | 0% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 4.67% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 0% | 0% | 0% | 0% | 0%
| Maximum allowed Depreciation | % | 90%
Depreciation (Tax)
| Rate of Depreciation (Book) | % | 13 | 0% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 7.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Maximum allowed Depreciation | % | 100%
Accelerated Depreciation
| Rate of Depreciation (Book) | % |  | 0% | 0% | 50% |  | 90% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
| Maximum allowed Depreciation | % | 90%
| Consider Acc Dep Benefits |  | FALSE
Additional O&M
|  | Rs Lakh |  |  |  | 2041-03-31: 0
Quarterly Assumptions for generation model
| Particulars | Units | Inputs | FY 2026 |  | 2030-03-31: FY 2027; 2034-03-31: FY 2028
|  |  | 2025-03-31 | 2025-06-30 | 2025-09-30 | 2025-12-31 | 2026-03-31 | 2026-06-30 | 2026-09-30 | 2026-12-31 | 2027-03-31 | 2027-06-30 | 2027-09-30 | 2027-12-31 | 2028-03-31 | 2028-06-30 | 2028-09-30 | 2028-12-31 | 2029-03-31 | 2029-06-30 | 2029-09-30 | 2029-12-31 | 2030-03-31 | 2030-06-30 | 2030-09-30 | 2030-12-31 | 2031-03-31 | 2031-06-30 | 2031-09-30 | 2031-12-31 | 2032-03-31 | 2032-06-30 | 2032-09-30 | 2032-12-31 | 2033-03-31
| Generation and Transmission | % | 90452.1803 | 0% | 3.513% | 2025-12-31: 10.48%; 2026-03-31: 37.66%; 2026-06-30: 40.26%; 2026-09-30: 8.088%
| Civil and Other Infastructure | % | 3238.6843 |  |  | 2025-12-31: 15%; 2026-03-31: 15%; 2026-06-30: 35%; 2026-09-30: 35%
| Other Cost | % | 9985.1586 |  |  | 2025-12-31: 5%; 2026-03-31: 5%; 2026-06-30: 45%; 2026-09-30: 45%
| sub total |  | 103676.0232
Solar Generation as per Erection Schedule
| Supply | 85%
| Module | % | 32919.2103 |  |  | 2026-03-31: 50%; 2026-06-30: 50%
| Floating System | % | 14000.0426 |  | 10% | 2025-12-31: 20%; 2026-03-31: 20%; 2026-06-30: 30%; 2026-09-30: 20%
| Anchoring Mooring System | % | 8885.679 |  | 20% | 2025-12-31: 60%; 2026-03-31: 20%
| UV/DC/AC/HT Cables | % | 3652.2621 |  |  | 2025-12-31: 30%; 2026-03-31: 30%; 2026-06-30: 30%; 2026-09-30: 10%
| Inverter & Inverter Duty Transformer | % | 10692.0951 |  |  | 2026-03-31: 50%; 2026-06-30: 50%
| HT Panels & MCR Equipments | % | 1253.2838 |  |  | 2026-03-31: 50%; 2026-06-30: 50%
| 220 KV PSS Equipments & Structures | % | 6539.673 |  |  | 2026-03-31: 50%; 2026-06-30: 50%
| Transmission Line | % | 961.2167 |  |  | 2026-03-31: 50%; 2026-06-30: 50%
| 220 KV Bay Activities | % | 358.7574 |  |  | 2026-03-31: 50%; 2026-06-30: 50%
| sub total |  | 79262.2199
| Erection & Commissioning Schedule | 15%
| Module | % | 4647.4179 |  |  | 2026-03-31: 20%; 2026-06-30: 40%; 2026-09-30: 40%
| Floating System | % | 1976.4766 |  |  | 2026-03-31: 20%; 2026-06-30: 40%; 2026-09-30: 40%
| Anchoring Mooring System | % | 1254.4488 |  |  | 2025-12-31: 20%; 2026-03-31: 40%; 2026-06-30: 40%
| UV/DC/AC/HT Cables | % | 515.6135 |  |  | 2026-03-31: 40%; 2026-06-30: 40%; 2026-09-30: 20%
| Inverter & Inverter Duty Transformer | % | 1509.4722 |  |  | 2026-06-30: 50%; 2026-09-30: 50%
| HT Panels & MCR Equipments | % | 176.9342 |  |  | 2026-06-30: 50%; 2026-09-30: 50%
| 220 KV PSS Equipments & Structures | % | 923.248 |  |  | 2026-06-30: 50%; 2026-09-30: 50%
| Transmission Line | % | 135.7012 |  |  | 2026-06-30: 50%; 2026-09-30: 50%
| 220 KV Bay Activities | % | 50.6481 |  |  | 2026-06-30: 50%; 2026-09-30: 50%
| sub total |  | 11189.9605
Solar Generation as per Erection Schedule
Supply
| Module | In Lacs | 32919.2103 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 16459.6052; 2026-06-30: 16459.6052; 2026-09-30: 0
| Floating System | In Lacs | 14000.0426 | 0 | 1400.0043 | 2025-12-31: 2800.0085; 2026-03-31: 2800.0085; 2026-06-30: 4200.0128; 2026-09-30: 2800.0085
| Anchoring Mooring System | In Lacs | 8885.679 | 0 | 1777.1358 | 2025-12-31: 5331.4074; 2026-03-31: 1777.1358; 2026-06-30: 0; 2026-09-30: 0
| UV/DC/AC/HT Cables | In Lacs | 3652.2621 | 0 | 0 | 2025-12-31: 1095.6786; 2026-03-31: 1095.6786; 2026-06-30: 1095.6786; 2026-09-30: 365.2262
| Inverter & Inverter Duty Transformer | In Lacs | 10692.0951 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 5346.0475; 2026-06-30: 5346.0475; 2026-09-30: 0
| HT Panels & MCR Equipments | In Lacs | 1253.2838 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 626.6419; 2026-06-30: 626.6419; 2026-09-30: 0
| 220 KV PSS Equipments & Structures | In Lacs | 6539.673 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 3269.8365; 2026-06-30: 3269.8365; 2026-09-30: 0
| Transmission Line | In Lacs | 961.2167 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 480.6083; 2026-06-30: 480.6083; 2026-09-30: 0
| 220 KV Bay Activities | In Lacs | 358.7574 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 179.3787; 2026-06-30: 179.3787; 2026-09-30: 0
|  |  | 79262.2199 | 0 | 3177.1401 | 2025-12-31: 9227.0945; 2026-03-31: 32034.9411; 2026-06-30: 31657.8095; 2026-09-30: 3165.2347
Erection & Commissioning
| Module | In Lacs | 4647.4179 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 929.4836; 2026-06-30: 1858.9672; 2026-09-30: 1858.9672
| Floating System | In Lacs | 1976.4766 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 395.2953; 2026-06-30: 790.5906; 2026-09-30: 790.5906
| Anchoring Mooring System | In Lacs | 1254.4488 | 0 | 0 | 2025-12-31: 250.8898; 2026-03-31: 501.7795; 2026-06-30: 501.7795; 2026-09-30: 0
| UV/DC/AC/HT Cables | In Lacs | 515.6135 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 206.2454; 2026-06-30: 206.2454; 2026-09-30: 103.1227
| Inverter & Inverter Duty Transformer | In Lacs | 1509.4722 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 0; 2026-06-30: 754.7361; 2026-09-30: 754.7361
| HT Panels & MCR Equipments | In Lacs | 176.9342 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 0; 2026-06-30: 88.4671; 2026-09-30: 88.4671
| 220 KV PSS Equipments & Structures | In Lacs | 923.248 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 0; 2026-06-30: 461.624; 2026-09-30: 461.624
| Transmission Line | In Lacs | 135.7012 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 0; 2026-06-30: 67.8506; 2026-09-30: 67.8506
| 220 KV Bay Activities | In Lacs | 50.6481 | 0 | 0 | 2025-12-31: 0; 2026-03-31: 0; 2026-06-30: 25.324; 2026-09-30: 25.324
|  |  | 11189.9605 | 0 | 0 | 2025-12-31: 250.8898; 2026-03-31: 2032.8038; 2026-06-30: 4755.5845; 2026-09-30: 4150.6823
| Total | In Lacs | 90452.1803 | 0 | 3177.1401 | 2025-12-31: 9477.9843; 2026-03-31: 34067.7449; 2026-06-30: 36413.3941; 2026-09-30: 7315.9171
| Final Capex Phasing |  |  | 0% | 3.513% | 2025-12-31: 10.48%; 2026-03-31: 37.66%; 2026-06-30: 40.26%; 2026-09-30: 8.088%
Economic Analysis
Economic Assumptions
| SCF | # | 0.92
| SWRF | # | 0.82887
| Unkilled Labour | % | 30%
| SERF | # | 1.087
| Unkilled Labour | INR/month | 9784
| Skilled Labour | INR/month | 11804
| Highly Skilled Labour | INR/month | 13023
|  |  |  | Please Select Switch | 1 | 2025-12-31: 2; 2026-06-30: 3; 2026-09-30: 4
| Avoided Fuel Cost |  |  | 2 | BkTPS | 2025-12-31: WBPDCL; 2026-06-30: Bandel TPS-I; 2026-09-30: Kolaghat TPS
| Net Generation- Thermal Plant-BKTPS | MU | 26494 |  | 6714 | 2025-12-31: 26494; 2026-06-30: 306.95; 2026-09-30: 4669.15
| Per Unit Cost of Coal | Rs/ kWh | 3.81 |  | 3.57 | 2025-12-31: 3.81; 2026-06-30: 4.6783; 2026-09-30: 4.1407
| Energy Charge | Rs/ kWh | 4 | Farakka I&II as per WBSEDCL TO for FY 24 to FY 25 | 2.37 | 2025-12-31: 2.41; 2026-06-30: 3.21; 2026-09-30: 2.88
| Fixed Charge | Rs Cr | 3688 |  | 799 | 2025-12-31: 3688; 2026-06-30: 4507; 2026-09-30: 58866
| Fixed Charge | Rs/ kWh | 1.4 |  | 1.2 | 2025-12-31: 1.4; 2026-06-30: 1.4683; 2026-09-30: 1.2607
| Escalation | % | 2%
| Reduced Carbon Emission |  |  |  | BkTPS | 2025-12-31: WBPDCL; 2026-06-30: Bandel TPS-I; 2026-09-30: Kolaghat TPS
| CO2 Emission | t-CO2 | 29868594.8332 | As per CEA | 7948550 | 2025-12-31: 29868594.8332; 2026-06-30: 226844; 2026-09-30: 3069718
| Economic Cost of CO2 emission | USD/tonne | 86 | India
| Current Exchange Rate | INR/USD | 83
| Economic Cost of CO2 emission | Rs / tonne | 7138
| Escalation | % | 0%
| Economic Discount Rate | % | 7.476%
Manpower Growth
| No of Manpower | No. | 60
| Escalation in Manpower | % | 1%
| Remuneration per person | Rs Cr | 0.02833
| Escalation in Remuneration | % | 3%
| Job Creation | No of Workers | Remuneration/Month (in INR)
| Estimates of the job creation potential during the solar park construction | 45 | 11804 | 15 per 100 MW
| Estimates of the job creation potential during the solar park operation and maintenance | 15 | 11804 | 5 per 100 mW
|  | 60 | 23608
Indirect Job Creation
Formulas:
Yes = DATE(YEAR(E176),MONTH(E176)+[Yes, row above],DAY(E176))
Yes = IF(MONTH([Yes, row above])<=3,DATE(YEAR([Yes, row above]),3,31),DATE(YEAR([Yes, row above])+1,3,31))
As per Design = EOMONTH([Yes],12)

## BOQ_G
| Summary | Unit | Unit Costs | Quantity | Cost (Rs Lakh) | Tax (Rs Lakh) | Cost with Tax (Rs Lakh) |  | Equipment Cost (Rs Lakhs) | Installation Cost (Rs Lakhs) | Total Cost (Rs per Wp) | Tax (Rs per Wp) | Gross Cost (Rs per Wp) | Cost (Rs Cr/ MW) |  | Equipment Cost (Rs Lakhs) | Installation Cost (Rs Lakhs) | Total Cost (Rs Lakhs) | Tax (Rs Lakhs) | Gross Cost (Rs Lakhs) |  | Equipment Cost | Installation Cost
A | PV Modules | Lot | 159 | 243.888 | 38728.4827 | 5344.5306 | 44073.0133 |  | 13.5 | 2.38 | 15.88 | 2.0484 | 17.9284 | 2.1685 |  | 32919.2103 | 4647.4179 | 37566.6282 | 5344.5306 | 44073.0133 |  | 85% | 12%
B | Inverters | Lot | 13 | 203.24 | 2650.5 | 365.769 | 3016.269 |  | 0.92 | 0.16 | 1.08 | 0.1392 | 1.2192 | 0.14841 |  | 2252.925 | 318.06 | 2570.985 | 365.769 | 3016.269 |  | 12% | 18%
C | Floating Structures and Installation | Lot | 135 | 243.888 | 32929.8607 | 4544.3208 | 37474.1815 |  | 11.48 | 2.03 | 13.51 | 1.743 | 15.253 | 1.8438 |  | 27990.3816 | 3951.5833 | 31941.9649 | 4544.3208 | 37474.1815 |  | 12.36%
1 | Float Structures |  | 68 | 243.888 | 16470.6383 | 2272.9481 | 18743.5864 |  | 5.74 | 1.01 | 6.75 | 0.87 | 7.62 | 0.92224 |  | 14000.0426 | 1976.4766 | 15976.5192 | 2272.9481 | 18743.5864
2 | Inverter Transformer System |  | 25 | 243.888 | 6005.4825 | 828.7566 | 6834.239 |  | 2.09 | 0.37 | 2.46 | 0.32 | 2.78 | 0.33626 |  | 5104.6601 | 720.6579 | 5825.318 | 828.7566 | 6834.239
3 | Anchoring & Mooring |  | 43 | 243.888 | 10453.74 | 1442.6161 | 11896.3561 |  | 3.64 | 0.64 | 4.28 | 0.55 | 4.83 | 0.58534 |  | 8885.679 | 1254.4488 | 10140.1278 | 1442.6161 | 11896.3561
D | Balance of System | Lot | 40 | 243.888 | 9694.1833 | 1337.7973 | 11031.9806 |  | 3.38 | 0.6 | 3.98 | 0.5136 | 4.4936 | 0.54281 |  | 8240.0558 | 1163.302 | 9403.3578 | 1337.7973 | 11031.9806
1 | DC - Cables, SCB, Accessories |  | 17 | 243.888 | 4077.46 | 562.6895 | 4640.1495 |  | 1.42 | 0.25 | 1.67 | 0.2154 | 1.8854 | 0.22831 |  | 3465.841 | 489.2952 | 3955.1362 | 562.6895 | 4640.1495
2 | AC Cables |  | 1 | 243.888 | 219.3188 | 30.266 | 249.5849 |  | 0.08 | 0.01 | 0.09 | 0.0114 | 0.1014 | 0.01228 |  | 186.421 | 26.3183 | 212.7393 | 30.266 | 249.5849
3 | Inverter Transformers, Switchgear and Panels |  | 16 | 243.888 | 3922.9529 | 541.3675 | 4464.3204 |  | 1.37 | 0.24 | 1.61 | 0.2076 | 1.8176 | 0.21966 |  | 3334.51 | 470.7543 | 3805.2643 | 541.3675 | 4464.3204
4 | Illumination System, Earthing |  | 4 | 243.888 | 1034.4515 | 142.7543 | 1177.2058 |  | 0.36 | 0.06 | 0.42 | 0.054 | 0.474 | 0.057922 |  | 879.2838 | 124.1342 | 1003.418 | 142.7543 | 1177.2058
5 | SCADA and Master Control Room |  | 2 | 243.888 | 440 | 60.5041 | 500.5041 |  | 0.15 | 0.03 | 0.18 | 0.0234 | 0.2034 | 0.024626 |  | 374 | 52.8 | 426.8 | 60.5041 | 500.5041
E | Civil Infrastructure | Lot | 7 | 243.888 | 1663.1343 | 229.5125 | 1892.6469 |  | 0.58 | 0.1 | 0.68 | 0.0876 | 0.7676 | 0.093124 |  | 1413.6642 | 199.5761 | 1613.2403 | 229.5125 | 1892.6469
| Building and Civil Infrastructure |  |  |  | 308.1343 | 42.5225 | 350.6569 |  | 0.11 | 0.02 | 0.13 | 0.0168 | 0.1468 | 0.017253 |  | 261.9142 | 36.9761 | 298.8903 | 42.5225 | 350.6569
| Marine Infrastructure |  |  |  | 280 | 38.64 | 318.64 |  | 0.1 | 0.02 | 0.12 | 0.0156 | 0.1356 | 0.015678 |  | 238 | 33.6 | 271.6 | 38.64 | 318.64
| Other Infrastructure |  |  |  | 1075 | 148.35 | 1223.35 |  | 0.37 | 0.07 | 0.44 | 0.057 | 0.497 | 0.060192 |  | 913.75 | 129 | 1042.75 | 148.35 | 1223.35
| FSP Project Capital Cost |  |  |  | 85666.1611 | 11821.9302 | 97488.0913 |  | 29.86 | 5.27 | 35.13 | 4.5318 | 39.6618 | 4.7967 |  | 72816.2369 | 10279.9393 | 83096.1763 | 11821.9302 | 97488.0913
| Other Costs (Designs, Survey, Insurance, Warranty, etc) |  |  |  | 2941.3852 | 405.9112 | 3347.2964 |  | 1.03 | 0.18 | 1.21 | 0.156 | 1.366 | 0.1647 |  | 2500.1775 | 352.9662 | 2853.1437 | 405.9112 | 3347.2964
| Grand Total |  |  |  | 88607.5463 | 12227.8414 | 100835.3877 |  | 30.88 | 5.45 | 36.33 | 4.6866 | 41.0166 | 4.9614 |  | 75316.4144 | 10632.9056 | 85949.3199 | 12227.8414 | 100835.3877
| Profit Margin |  |  |  | 6508.2021 | 898.1319 | 7406.334 |  | 2.27 | 0.4 | 2.67 | 0.3444 | 3.0144 | 0.36441 |  | 5531.9718 | 780.9843 | 6312.9561 | 898.1319 | 7406.334
| FSPV Total |  |  |  | 95115.7485 | 13125.9733 | 108241.7218 |  | 33.15 | 5.85 | 39 | 5.031 | 44.031 | 5.3258 |  | 80848.3862 | 11413.8898 | 92262.276 | 13125.9733 | 108241.7218
| Optional |  |  |  | 638.8 | 88.1544 | 726.9544 |  | 0.22 | 0.04 | 0.26 | 0.0336 | 0.2936 | 0.035768 |  | 542.98 | 76.656 | 619.636 | 88.1544 | 726.9544
0
| General |  |  | #
| Project Capacity | MW DC |  | 243.888
| Project Capacity | MW AC |  | 203.24
| Inverter Rating (in kW) & Qty (At 50ᵒ C Temp) | 4400 |  | 44
| Inverter Rating (in kW) & Qty (At 50ᵒ C Temp) | 1100 |  | 12
| Total Modules | # |  | 420544
| Module rating | Wp |  | 580
| # Module per string | # |  | 28 | [5 empty] | 2.91
| BOQ | [12 empty] | Tax Rate
A | PV Modules
1 | PV Modules | # | 9187.2 | 420544 | 38636.2184 | 5331.7981 | 43968.0165 |  | 13.47 | 2.38 | 15.85 | 2.0448 | 17.8948 | 13.8% |  | 32840.7856 | 4636.3462 | 37477.1318 | 5331.7981 | 43968.0165
2 | Spare Modules | # | 9187.2 | 841 | 77.2644 | 10.6625 | 87.9268 |  | 0.03 | 0 | 0.03 | 0.0036 | 0.0336 | 13.8% |  | 65.6747 | 9.2717 | 74.9464 | 10.6625 | 87.9268
3 | EL Testing | # | 1000000 | 1 | 10 | 1.38 | 11.38 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 8.5 | 1.2 | 9.7 | 1.38 | 11.38
4 | Thermography | # | 500000 | 1 | 5 | 0.69 | 5.69 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 4.25 | 0.6 | 4.85 | 0.69 | 5.69
B | Inverters
1 | Inverter 4.4 MW | # | 5700000 | 44 | 2508 | 346.104 | 2854.104 |  | 0.87 | 0.15 | 1.02 | 0.1314 | 1.1514 | 13.8% |  | 2131.8 | 300.96 | 2432.76 | 346.104 | 2854.104
2 | Inverter 1.1 MW | # | 1187500 | 12 | 142.5 | 19.665 | 162.165 |  | 0.05 | 0.01 | 0.06 | 0.0078 | 0.0678 | 13.8% |  | 121.125 | 17.1 | 138.225 | 19.665 | 162.165
C | Floating Module Mounting Structure
C1 | Floating Structures | [7 empty] | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
1 | OMF (Module Float) | Rs per float | 1045 | 420544 | 4394.6848 | 606.4665 | 5001.1513 |  | 1.53 | 0.27 | 1.8 | 0.2322 | 2.0322 | 13.8% |  | 3735.4821 | 527.3622 | 4262.8443 | 606.4665 | 5001.1513
2 | OMWF (Main Walkway Float) | Rs per float | 4018.5 | 48032 | 1930.1659 | 266.3629 | 2196.5288 |  | 0.67 | 0.12 | 0.79 | 0.102 | 0.892 | 13.8% |  | 1640.641 | 231.6199 | 1872.2609 | 266.3629 | 2196.5288
3 | OLSF (Long Secondary Float) | Rs per float | 2411.1 | 163308 | 3937.5192 | 543.3776 | 4480.8968 |  | 1.37 | 0.24 | 1.61 | 0.2076 | 1.8176 | 13.8% |  | 3346.8913 | 472.5023 | 3819.3936 | 543.3776 | 4480.8968
4 | OSSF (Small Secondary Float) | Rs per float | 1607.4 | 148016 | 2379.2092 | 328.3309 | 2707.5401 |  | 0.83 | 0.15 | 0.98 | 0.1266 | 1.1066 | 13.8% |  | 2022.3278 | 285.5051 | 2307.8329 | 328.3309 | 2707.5401
5 | OSSFx (Small Secondary Walkway Float) | Rs per float | 7968.125 | 24096 | 1919.9994 | 264.9599 | 2184.9593 |  | 0.67 | 0.12 | 0.79 | 0.102 | 0.892 | 13.8% |  | 1631.9995 | 230.3999 | 1862.3994 | 264.9599 | 2184.9593
6 | OCF (Cable Float)-DC | Rs per float | 126.35 | 755372 | 954.4125 | 131.7089 | 1086.1215 |  | 0.33 | 0.06 | 0.39 | 0.0504 | 0.4404 | 13.8% |  | 811.2506 | 114.5295 | 925.7801 | 131.7089 | 1086.1215
7 | OCF (Cable Float)-AC | Rs per float | 105.45 | 905308 | 954.6473 | 131.7413 | 1086.3886 |  | 0.33 | 0.06 | 0.39 | 0.0504 | 0.4404 | 13.8% |  | 811.4502 | 114.5577 | 926.0079 | 131.7413 | 1086.3886
C2 | Inverter Transformer Platforms
1 | Transformer of Size 5.5 MVA | Rs per Transformer | 5790250 | 12 | 694.83 | 95.8865 | 790.7165 |  | 0.24 | 0.04 | 0.28 | 0.036 | 0.316 | 13.8% |  | 590.6055 | 83.3796 | 673.9851 | 95.8865 | 790.7165
2 | Transformer of Size 6.5 MVA | Rs per Transformer | 6992000 | 32 | 2237.44 | 308.7667 | 2546.2067 |  | 0.78 | 0.14 | 0.92 | 0.1188 | 1.0388 | 13.8% |  | 1901.824 | 268.4928 | 2170.3168 | 308.7667 | 2546.2067
3 | Platform-Ferro Cement | Rs per Platform | 5500000 | 52 | 2860 | 394.68 | 3254.68 |  | 1 | 0.18 | 1.18 | 0.1524 | 1.3324 | 13.8%
4 | Inverter Barge- Mooring Line length | Rs. Per KM | 1055716.285 | 11.88 | 213.2125 | 29.4233 | 242.6358 |  | 0.07 | 0.01 | 0.08 | 0.0102 | 0.0902 | 13.8% |  | 181.2306 | 25.5855 | 206.8161 | 29.4233 | 242.6358
C3 | Anchoring and Mooring System
1 | Mooring System | Rs per KM | 5878028.1 | 158.48 | 9315.4989 | 1285.5389 | 10601.0378 |  | 3.25 | 0.57 | 3.82 | 0.4926 | 4.3126 | 13.8% |  | 7918.1741 | 1117.8599 | 9036.034 | 1285.5389 | 10601.0378
2 | Mooring Line Accessories | Rs per unit | 7505 | 2400 | 180.12 | 24.8566 | 204.9766 |  | 0.06 | 0.01 | 0.07 | 0.009 | 0.079 | 13.8% |  | 153.102 | 21.6144 | 174.7164 | 24.8566 | 204.9766
3 | Anchor System | Rs per Anchor | 17307.1 | 5536 | 958.1211 | 132.2207 | 1090.3418 |  | 0.33 | 0.06 | 0.39 | 0.0504 | 0.4404 | 13.8% |  | 814.4029 | 114.9745 | 929.3774 | 132.2207 | 1090.3418
D | Balance of System (BoS)
D1 | DC Cables & Connectors
1 | 1.8 kV DC, 1Cx 6 Sq.mm. string cables in line with EN50618 | m | 58 | 1302246.4 | 755.3029 | 104.2318 | 859.5347 |  | 0.26 | 0.05 | 0.31 | 0.0402 | 0.3502 | 13.8% |  | 642.0075 | 90.6363 | 732.6438 | 104.2318 | 859.5347
2 | String cable dressing | # | 5 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
D2 | DC Connectors
1 | Male - MC4 Connector for 1.8 kV DC, 6 Sq.mm. string cables with spare | # | 93 | 17338 | 16.1243 | 2.2252 | 18.3495 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 13.7057 | 1.9349 | 15.6406 | 2.2252 | 18.3495
2 | FeMale - MC4 Connector for 1.8 kV DC, 6 Sq.mm. string cables with spare | # | 93 | 17338 | 16.1243 | 2.2252 | 18.3495 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 13.7057 | 1.9349 | 15.6406 | 2.2252 | 18.3495
3 | Cable Ties-300 mm | # | 141 | 1000 | 1.41 | 0.19458 | 1.6046 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.1985 | 0.1692 | 1.3677 | 0.19458 | 1.6046
4 | Cable Ties-550 mm | # | 370 | 1000 | 3.7 | 0.5106 | 4.2106 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 3.145 | 0.444 | 3.589 | 0.5106 | 4.2106
5 | 32 ID / 40mm OD DWC Pipe (UV Protection & Helogen Free) | m | 150 | 145800 | 218.7 | 30.1806 | 248.8806 |  | 0.08 | 0.01 | 0.09 | 0.0114 | 0.1014 | 13.8% |  | 185.895 | 26.244 | 212.139 | 30.1806 | 248.8806
6 | Fuse Connectors-30 A | # | 275 | 17338 | 47.6795 | 6.5798 | 54.2593 |  | 0.02 | 0 | 0.02 | 0.0024 | 0.0224 | 13.8% |  | 40.5276 | 5.7215 | 46.2491 | 6.5798 | 54.2593
7 | Precast Chambers | # | 10000 | 100 | 10 | 1.38 | 11.38 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 8.5 | 1.2 | 9.7 | 1.38 | 11.38
D3 | DC Accessories
1 | 1.8 kV, 1Cx300 Sq.mm. Aluminium Conductor, XLPE insulated, (1.5% loss) | # | 462.65 | 528000 | 2442.792 | 337.1053 | 2779.8973 |  | 0.85 | 0.15 | 1 | 0.129 | 1.129 | 13.8% |  | 2076.3732 | 293.135 | 2369.5082 | 337.1053 | 2779.8973
2 | Termination Kits for above-3.3 kV at inverter end - Gland for 300 sqmm Cable | # | 921 | 1354.5 | 12.4749 | 1.7215 | 14.1965 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 10.6037 | 1.497 | 12.1007 | 1.7215 | 14.1965
3 | Lugs for above cable including inverter end - Lugs for 300 sqmm Cable | # | 300 | 2709 | 8.127 | 1.1215 | 9.2485 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 6.908 | 0.97524 | 7.8832 | 1.1215 | 9.2485
D4 | String Monitoring Box (SMB)
1 | DC disconnector - 400A, 2P; Fuse - 30A on positive side without Y connector; SPD Class 2, Metal gland | # | 75000 | 688 | 516 | 71.208 | 587.208 |  | 0.18 | 0.03 | 0.21 | 0.027 | 0.237 | 13.8% |  | 438.6 | 61.92 | 500.52 | 71.208 | 587.208
2 | Painting & Naming over SCB | # | 100 | 645 | 0.645 | 0.08901 | 0.73401 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.54825 | 0.0774 | 0.62565 | 0.08901 | 0.73401
3 | Structure for mounting SCB with canopy | # | 4400 | 645 | 28.38 | 3.9164 | 32.2964 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 24.123 | 3.4056 | 27.5286 | 3.9164 | 32.2964
D5 | AC Cables
D5.1 | AC Cables (1.9/3.3kV) - From Inverter - Inverter Transformer
1 | Al 1Cx400Sq.mm, 1.9/3.3kV, Al, Ar, XLPE, FRLS Inner Sheath & Outer Sheath On Cable Tray | Mtr | 564 | 22325 | 125.913 | 17.376 | 143.289 |  | 0.04 | 0.01 | 0.05 | 0.0066 | 0.0566 | 13.8% |  | 107.026 | 15.1096 | 122.1356 | 17.376 | 143.289
2 | 450x125mmx2mm thk Ladder Type HDG Cable Tray with GI Cover | Mtr | 480 | 3500 | 16.8 | 2.3184 | 19.1184 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 14.28 | 2.016 | 16.296 | 2.3184 | 19.1184
3 | 50x6 MM GI Earth Strip for cable tray earthing with galvanization of min 80 microns | Mtr | 56 | 2500 | 1.4 | 0.1932 | 1.5932 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.19 | 0.168 | 1.358 | 0.1932 | 1.5932
4 | Trefoil clamp-Nylon6 glass filled fibre clamp for 1Cx400 Sq.mm cable | NOS | 95 | 5330 | 5.0635 | 0.69876 | 5.7623 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 4.304 | 0.60762 | 4.9116 | 0.69876 | 5.7623
5 | 4Cx 16Sqmm Al,Ar, XLPE with Cable for Peripherial lighting, FRLSH | Meters | 108 | 20700 | 22.356 | 3.0851 | 25.4411 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 19.0026 | 2.6827 | 21.6853 | 3.0851 | 25.4411
6 | 4Cx 16 Sqmm, Al, cable with Cable from light DB to fisrt light pole, FRLSH | Meters | 108 | 3900 | 4.212 | 0.58126 | 4.7933 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 3.5802 | 0.50544 | 4.0856 | 0.58126 | 4.7933
7 | Al 4c, 16sqmm, Al, Ar, XLPE FRLSH outer & Inner sheath | Meters | 108 | 2350 | 2.538 | 0.35024 | 2.8882 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 2.1573 | 0.30456 | 2.4619 | 0.35024 | 2.8882
8 | Al 1Cx400Sq.mm, 1.9/3.3kV, Al, Ar, XLPE, FRLS outersheath On Cable Tray | Mters | 564 | 750 | 4.23 | 0.58374 | 4.8137 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 3.5955 | 0.5076 | 4.1031 | 0.58374 | 4.8137
9 | Trefoil clamp-Nylon6 glass filled fibre clamp for 1Cx400 Sq.mm cable | NOS | 95 | 280 | 0.266 | 0.036708 | 0.30271 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.2261 | 0.03192 | 0.25802 | 0.036708 | 0.30271
10 | 3Cx2.5 Sq.mm Cu. Flexible cable from JB to Light fixture | Meters | 75 | 1679 | 1.2592 | 0.17378 | 1.433 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.0704 | 0.15111 | 1.2215 | 0.17378 | 1.433
D5.2 | Control Cable
1 | 3CX2.5, Cu, Ar, XLPE with FRLSH outer & Inner sheath | Meters | 107 | 600 | 0.642 | 0.088596 | 0.7306 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.5457 | 0.07704 | 0.62274 | 0.088596 | 0.7306
2 | 5CX2.5, Cu, Ar, XLPE with FRLSH outer & Inner sheath | Meters | 125 | 5560 | 6.95 | 0.9591 | 7.9091 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 5.9075 | 0.834 | 6.7415 | 0.9591 | 7.9091
3 | 7CX2.5, Cu, Ar, XLPE with FRLSH outer & Inner sheath | Meters | 140 | 1060 | 1.484 | 0.20479 | 1.6888 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.2614 | 0.17808 | 1.4395 | 0.20479 | 1.6888
4 | 10CX2.5, Cu, Ar, XLPE with FRLSH outer & Inner sheath | Meters | 100 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
5 | 1.1 KV, YWY, 14C X 2.5 Sq.mm Electrolytic Grade annealed plain copper, EXTRUDED HR PVC TYPE -C INSULATION AS PER IS : 5831 -1984, Extruded PVC TYPE ST-2 AS PER IS : 5831 1-984 innersheath, GS round wire, EXTRUDED FR-LSH PVC TYPE ST-2 outersheath cable | Meters | 220 | 600 | 1.32 | 0.18216 | 1.5022 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.122 | 0.1584 | 1.2804 | 0.18216 | 1.5022
6 | 16X2.5, Cu, Ar, XLPE with FRLSH outer & Inner sheath | Meters | 150 | 4700 | 7.05 | 0.9729 | 8.0229 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 5.9925 | 0.846 | 6.8385 | 0.9729 | 8.0229
7 | 1.1 KV, YWY, 19C X 2.5 Sq.mm Electrolytic Grade annealed plain copper, EXTRUDED HR PVC TYPE -C INSULATION AS PER IS : 5831 -1984, Extruded PVC TYPE ST-2 AS PER IS : 5831 1-984 innersheath, GS round wire, EXTRUDED FR-LSH PVC TYPE ST-2 outersheath cable | Meters | 190 | 600 | 1.14 | 0.15732 | 1.2973 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.969 | 0.1368 | 1.1058 | 0.15732 | 1.2973
D5.3 | Cable tray
2 | 300x125mmx2mm thk Ladder Type HDG Cable Tray with GI Cover | Mtr | 320 | 240 | 0.768 | 0.10598 | 0.87398 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.6528 | 0.09216 | 0.74496 | 0.10598 | 0.87398
3 | 600mmx150mmx2mm Ladder type tray | Mtr | 550 | 100 | 0.55 | 0.0759 | 0.6259 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.4675 | 0.066 | 0.5335 | 0.0759 | 0.6259
D5.4 | Perforated cable tray
2 | 300mm W x 50mm H x 2mm Thk Hot dip Galvanised Perforated type Cable Tray GI Hot Dip Galvanised as per with Zinc coating of 610GSM & 86 Micron Average as per IS:4759,2629 | Mtr | 340 | 800 | 2.72 | 0.37536 | 3.0954 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 2.312 | 0.3264 | 2.6384 | 0.37536 | 3.0954
3 | 150mm W x 50mm H x 2mm Thk Galvanised Perforated type Cable Tray GI Hot Dip Galvanised as per with Zinc coating of 610GSM & 86 Micron Average as per IS:4759,2629 | Mtr | 245 | 800 | 1.96 | 0.27048 | 2.2305 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.666 | 0.2352 | 1.9012 | 0.27048 | 2.2305
4 | Cable tray supports | KG | 120 | 7760 | 9.312 | 1.2851 | 10.5971 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 7.9152 | 1.1174 | 9.0326 | 1.2851 | 10.5971
D5.5 | Hume Pipe | [7 empty] | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
1 | Dwc pipe for external lighting entry/exit | MTR | 45 | 3078 | 1.3851 | 0.19114 | 1.5762 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.1773 | 0.16621 | 1.3435 | 0.19114 | 1.5762
2 | 150mm Dia Hume Pipe - 2mtr length | MTR | 0 | 693 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
3 | 200mm Dia Hume Pipe - 2mtr length | MTR | 0 | 2104.2 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
4 | 300 mm dia, Class-2 Hume pipe | MTR | 0 | 352 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
C-5 | Inverter Transformers
1 | Inverter Transformer [Type-A] Outdoor Oil type. Rating : 8.8 MVA, 33/2x0.660 kV, 3 Winding Al. Trafo., Dy11y11 Floating neutral. 1.7A/Sq.mm current density. 1.0 % Loss (0.9 % load loss + 0.1% No load loss) with SC tested transformer. | NOS | 11537750 | 17 | 1961.4175 | 270.6756 | 2232.0931 |  | 0.68 | 0.12 | 0.8 | 0.1032 | 0.9032 | 13.8% |  | 1667.2049 | 235.3701 | 1902.575 | 270.6756 | 2232.0931
2 | Inverter Transformer [ Type-A] Outdoor Oil type. Rating : 6.3 MVA, 33/2x0.660 kV, 3 Winding Al. Trafo., Dy11y11 Floating neutral. 1.7A/Sq.mm current density. 1.0 % Loss (0.9 % load loss + 0.1% No load loss) with SC tested transformer. | NOS | 9180000 | 6 | 550.8 | 76.0104 | 626.8104 |  | 0.19 | 0.03 | 0.22 | 0.0282 | 0.2482 | 13.8% |  | 468.18 | 66.096 | 534.276 | 76.0104 | 626.8104
3 | NIPFS for the Above | NOS | 130000 | 23 | 29.9 | 4.1262 | 34.0262 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 25.415 | 3.588 | 29.003 | 4.1262 | 34.0262
C-6 | HT Panels & RMU | [7 empty] | 0 | 0 | 0 | 0 | 0 | 13.8%
1 | 33kV Outdoor Type ICOG PANEL-IP 55, 630A Al.Busbar 630A VCB, EDO with earthswitch & Surge Arrestor. IAC tested for 25 KA, CT, PT , Instant /OverCurrent & Earthfault protection relays, & metering with Selector switches. DC Power pack for control supply | Nos | 919240 | 22 | 202.2328 | 27.9081 | 230.1409 |  | 0.07 | 0.01 | 0.08 | 0.0102 | 0.0902 | 13.8% |  | 171.8979 | 24.2679 | 196.1658 | 27.9081 | 230.1409
2 | 33 kV Outdoor-IP 55 , 4 Panel 2 I/C LBS with ES, 1 630A VCB I/C, 630A Al.Busbar & 1 O/G 630A LBS with ES. CT, PT , Instant /OverCurrent & Earthfault protection relays, & metering with Selector switches. Internal Arc sensors to be considered for all feeders. DC power pack for Control Supply | Nos | 2000000 | 6 | 120 | 16.56 | 136.56 |  | 0.04 | 0.01 | 0.05 | 0.0066 | 0.0566 | 13.8% |  | 102 | 14.4 | 116.4 | 16.56 | 136.56
3 | 33 kV Outdoor-IP 55 , 3 Panel 1 I/C 630A VCB , 1 I/C LBS with ES, 630A Al.Busbar & 1 O/G 630 A LBS with ES. CT, PT , Instant /OverCurrent & Earthfault protection relays, & metering with Selector switches. Internal Arc sensors to be considered for all feeders. DC power pack for Control Supply | Nos | 1500000 | 1 | 15 | 2.07 | 17.07 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 12.75 | 1.8 | 14.55 | 2.07 | 17.07
4 | 33 kV Indoor-IP 20 , 15 Panel 31.5KA/ sec 8 I/C 630A VCB (PV Park) , 2 VCB 630A Aux, 2x 2500A Al.Busbar, 2 O/G 2500 A VCB with ES & Surge Arrestor, 2 BBPT, 1 B/C 2500A. CT, PT , Instant /OverCurrent & Earthfault protection relays, undervoltage / overvoltage, Master Trip relay. Power Quality meter, MFM with Selector switches. Sp Charging for O/G feeder. IAC 31.5kA/ sec or Internal Arc sensors to be considered for all feeders. 110V Battery charger for control supply | Nos | 17546960 | 1 | 175.4696 | 24.2148 | 199.6844 |  | 0.06 | 0.01 | 0.07 | 0.009 | 0.079 | 13.8% |  | 149.1492 | 21.0564 | 170.2055 | 24.2148 | 199.6844
E | HT Cables & Terminations
1 | 19/33 kV[E], 1Cx400 Sq.mm, Aluminium Conductor, XLPE insulated, Armoured, Armour+Sheath - 25 kA for 0.5 sec., FR Inner & outer sheath From 4 Panel board to Main HT panel | Mtr | 1070 | 44500 | 476.15 | 65.7087 | 541.8587 |  | 0.17 | 0.03 | 0.2 | 0.0258 | 0.2258 | 13.8% |  | 404.7275 | 57.138 | 461.8655 | 65.7087 | 541.8587
2 | 19/33 kV[E], 1Cx240 Sq.mm, Aluminium Conductor, XLPE insulated, Armoured, Armour+Sheath - 31.5 kA for 0.5 sec., FR Inner & outer sheath From 4 Panel board to Main HT panel | Nos | 866 | 26800 | 232.088 | 32.0281 | 264.1161 |  | 0.08 | 0.01 | 0.09 | 0.0114 | 0.1014 | 13.8% |  | 197.2748 | 27.8506 | 225.1254 | 32.0281 | 264.1161
3 | Indoor Termination 1Cx400 Sq.mm | Nos | 3000 | 30 | 0.9 | 0.1242 | 1.0242 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.765 | 0.108 | 0.873 | 0.1242 | 1.0242
4 | Outdoor Termination 1Cx400 Sq.mm | Nos | 3000 | 27 | 0.81 | 0.11178 | 0.92178 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.6885 | 0.0972 | 0.7857 | 0.11178 | 0.92178
5 | Outdoor Termination 1Cx240 Sq.mm | Mtr | 5000 | 210 | 10.5 | 1.449 | 11.949 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 8.925 | 1.26 | 10.185 | 1.449 | 11.949
6 | Straight through Joint 3Cx300 Sq.mm | Nos | 5000 | 38 | 1.9 | 0.2622 | 2.1622 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.615 | 0.228 | 1.843 | 0.2622 | 2.1622
7 | 19/33 kV[E], 1Cx400 Sq.mm, Aluminium Conductor, XLPE insulated, Armoured, Armour - 25 kA for 0.5 sec,, FRLSH Inner & outer sheath on tray From Main HT Panel to Power transformer | Nos | 1070 | 800 | 8.56 | 1.1813 | 9.7413 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 7.276 | 1.0272 | 8.3032 | 1.1813 | 9.7413
8 | Indoor Termination | Nos | 3000 | 20 | 0.6 | 0.0828 | 0.6828 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.51 | 0.072 | 0.582 | 0.0828 | 0.6828
9 | Outdoor Termination |  | 5000 | 20 | 1 | 0.138 | 1.138 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.85 | 0.12 | 0.97 | 0.138 | 1.138
10 | Straight throgh Joint |  | 1000 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
11 | Trefoil clamp-Nylon6 glass filled fibre clamp for 1Cx400 Sq.mm cable | NOS | 100 | 525 | 0.525 | 0.07245 | 0.59745 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.44625 | 0.063 | 0.50925 | 0.07245 | 0.59745
F | LT System & Auxiliary System
1 | Auxiliary Transformer (5 kVA, 660/415 V) With Isolator in Each ICR - Dry type , 2.5% of rated capacity as losses, | Nos | 40000 | 22 | 8.8 | 1.2144 | 10.0144 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 7.48 | 1.056 | 8.536 | 1.2144 | 10.0144
2 | Aux DB for above Trafo | Nos | 70000 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
3 | Auxilary Transformer (100 kVA, 33kV/415V) With Isolator in MCR - oil type, as per IS1180. level-2. Current density 3A, Earth strip should be suitable for STC for 4 sec. | Nos | 225000 | 2 | 4.5 | 0.621 | 5.121 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 3.825 | 0.54 | 4.365 | 0.621 | 5.121
4 | Aux DB for above Trafo | Nos |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
5 | 4Way TPN L+PDB MCR, IVR & Security room -IP 52 | Nos | 10000 | 2 | 0.2 | 0.0276 | 0.2276 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.17 | 0.024 | 0.194 | 0.0276 | 0.2276
6 | Main Aux. panel - MCR with provision for 2 I/C's from Aux Trafo, 1no. BC , 1 I/C for DG incomer.-IP 42, Current density- 0.5A/Sq.mm, MCCB with 50kA, LSIG release at incomer of ACDB Short circuit Raring will be 50kA/1SEC | No. |  | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
7 | Inv room Aux. panel (Indoor type) with Minimum 16Nos. MCCB output feeder, installed in PEB building-IP 52, Current density- 0.5A/Sq.mm, MCCB with 50kA, LSIG release at incomer of ACDB Short circuit Raring will be 50kA/1SEC | No. | 150000 | 22 | 33 | 4.554 | 37.554 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 28.05 | 3.96 | 32.01 | 4.554 | 37.554
8 | Isolator / COS Panel- -IP 52, Current density- 0.5A/Sq.mm | No. | 40000 | 22 | 8.8 | 1.2144 | 10.0144 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 7.48 | 1.056 | 8.536 | 1.2144 | 10.0144
9 | UPS Panel for Main Control room -IP 52, Current density- 0.5A/Sq.mm | Nos | 200000 | 22 | 44 | 6.072 | 50.072 |  | 0.02 | 0 | 0.02 | 0.0024 | 0.0224 | 13.8% |  | 37.4 | 5.28 | 42.68 | 6.072 | 50.072
10 | UPS Panel for Inverter Station -IP 52, Current density- 0.5A/Sq.mm | Nos | 200000 | 1 | 2 | 0.276 | 2.276 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.7 | 0.24 | 1.94 | 0.276 | 2.276
11 | LDB for main control room & Hostel Building -IP 42, with 24hours timer and RCCB as Incomer, for each phase and O/G MCB's | Nos | 100000 | 1 | 1 | 0.138 | 1.138 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.85 | 0.12 | 0.97 | 0.138 | 1.138
12 | PDB for main control room & Hostel Building -IP 42 | Nos | 70000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
13 | ELDB for main control room & Hostel Building -IP-42, with 24hours timer and RCCB as Incomer, for each phase and O/G MCB's | Nos | 80000 | 1 | 0.8 | 0.1104 | 0.9104 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.68 | 0.096 | 0.776 | 0.1104 | 0.9104
14 | EPDB for main control room & Hostel Building -IP 42 | Nos |  | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
15 | Lighting transformer - 2kVA - 415V/415V | Nos | 15000 | 8 | 1.2 | 0.1656 | 1.3656 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 1.02 | 0.144 | 1.164 | 0.1656 | 1.3656
16 | Lighting transformer - 5kVA - 415V/415V | Nos | 22000 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
17 | Raw power -LDB for Inverter station -IP 52 with 24hours timer and RCCB as Incomer, for each phase and O/G MCB's | Nos | 70000 | 22 | 15.4 | 2.1252 | 17.5252 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 13.09 | 1.848 | 14.938 | 2.1252 | 17.5252
18 | UPS power -ELDB for Inverter station -IP 52 with 24hours timer and RCCB as Incomer, for each phase and O/G MCB's | Nos | 70000 | 22 | 15.4 | 2.1252 | 17.5252 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 13.09 | 1.848 | 14.938 | 2.1252 | 17.5252
19 | 110V Battery charger & 2 set of Battery racks | Nos | 500000 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
20 | Main Aux. panel (Indoor type) with separate KWH meter-IP 52, Current density- 0.5A/Sq.mm for Hostel | Nos | 100000 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
G1 | Earthing System
1 | Under Water Dead Weight Earthing | Set | 30 | 264844.8 | 79.4534 | 10.9646 | 90.418 |  | 0.03 | 0 | 0.03 | 0.0036 | 0.0336 | 13.8% |  | 67.5354 | 9.5344 | 77.0698 | 10.9646 | 90.418
2 | 50x10 GS earth strip | Mtr | 206 | 89971.2 | 185.3407 | 25.577 | 210.9177 |  | 0.06 | 0.01 | 0.07 | 0.009 | 0.079 | 13.8% |  | 157.5396 | 22.2409 | 179.7805 | 25.577 | 210.9177
3 | 65x10 MM GI Earth Strip | Mtr | 7000 | 288 | 20.16 | 2.7821 | 22.9421 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 17.136 | 2.4192 | 19.5552 | 2.7821 | 22.9421
4 | 25x6 MM GI Earth Strip | Mtr | 755 | 18216 | 137.5308 | 18.9793 | 156.5101 |  | 0.05 | 0.01 | 0.06 | 0.0078 | 0.0678 | 13.8% |  | 116.9012 | 16.5037 | 133.4049 | 18.9793 | 156.5101
5 | 25x3 MM GI Earth Strip | Mtr | 7000 | 90 | 6.3 | 0.8694 | 7.1694 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 5.355 | 0.756 | 6.111 | 0.8694 | 7.1694
6 | 50x6 MM Cu Earth Strip | Mtr | 206 | 480 | 0.9888 | 0.13645 | 1.1253 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.84048 | 0.11866 | 0.95914 | 0.13645 | 1.1253
7 | 25x3 MM Cu Earth Strip | Mtr | 206 | 2880 | 5.9328 | 0.81873 | 6.7515 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 5.0429 | 0.71194 | 5.7548 | 0.81873 | 6.7515
8 | 25x6 MM GI/Cu Flexible Cable | Mtr | 10 | 480 | 0.048 | 0.006624 | 0.054624 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.0408 | 0.00576 | 0.04656 | 0.006624 | 0.054624
9 | 50x6 MM GI Earth Strip for HT trench | Mtr | 35 | 7660 | 2.681 | 0.36998 | 3.051 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 2.2788 | 0.32172 | 2.6006 | 0.36998 | 3.051
G2 | Lightning Protection with Earthing
1 | Earth Pit - 3nos. Per LA 3000mm 17.2mm dia copper bonded rod along with earth pit & maintenace free earthing | NOS | 1200 | 16320 | 195.84 | 27.0259 | 222.8659 |  | 0.07 | 0.01 | 0.08 | 0.0102 | 0.0902 | 13.8% |  | 166.464 | 23.5008 | 189.9648 | 27.0259 | 222.8659
2 | Franklin Rod Type LA System | NOS | 1000 | 24480 | 244.8 | 33.7824 | 278.5824 |  | 0.09 | 0.02 | 0.11 | 0.0144 | 0.1244 | 13.8% |  | 208.08 | 29.376 | 237.456 | 33.7824 | 278.5824
3 | 7.5 mtr lightning mast | NOS |  | 7500 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
4 | 2.5 mtr lightning mast | NOS |  | 5000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
5 | Electromechanical Lightning Event Counter (4 DIGIT) in weather proof enclosure | NOS |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
3 | Down Conductor - 1cx70Sq.mm Cu flexible cable - green colour | Mtr | 60 | 122400 | 73.44 | 10.1347 | 83.5747 |  | 0.03 | 0 | 0.03 | 0.0036 | 0.0336 | 13.8% |  | 62.424 | 8.8128 | 71.2368 | 10.1347 | 83.5747
4 | Bimetallic lugs for connecting cable and Earth strip | Incl above |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
5 | 1Cx25 Sq.mm. Cu. Flexible Cable For SCB | Mtr | 1200 | 88 | 1.056 | 0.14573 | 1.2017 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.8976 | 0.12672 | 1.0243 | 0.14573 | 1.2017
6 | Cu Lugs for above | Nos. | 1000 | 88 | 0.88 | 0.12144 | 1.0014 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0.748 | 0.1056 | 0.8536 | 0.12144 | 1.0014
G3 | Illumination System & Security System | [7 empty] | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
1 | Plant Illumination System | Set | 3000 | 2000 | 60 | 8.28 | 68.28 |  | 0.02 | 0 | 0.02 | 0.0024 | 0.0224 | 13.8% |  | 51 | 7.2 | 58.2 | 8.28 | 68.28
2 | CCTV | Set | 5000 | 400 | 20 | 2.76 | 22.76 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 17 | 2.4 | 19.4 | 2.76 | 22.76
H1 | SCADA | [7 empty] | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
1 | SCADA Lumsum Cost | NOS | 1000000 | 44 | 440 | 60.72 | 500.72 |  | 0.15 | 0.03 | 0.18 | 0.0234 | 0.2034 | 13.8% |  | 374 | 52.8 | 426.8 | 60.72 | 500.72
2 | Power Plant Controller | NOS | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
3 | communication, s/w, h/w) | NOS | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
4 | Communication cable-CAT-6 cable for SCADA | MTR | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
5 | Fiber Optic Cable for SCADA between Inv. Station to MCR - 12 fibre | MTR | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
6 | DWC Pipe for OFC cable- 32mm ID / 40mm OD (DWC pipe required for OFC cable) | MTR | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
7 | Dedicated UPS for SCADA servers (5KVA) | MTR | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
8 | RS485 Communication Cable 2Px0.5 sqmm Shielded GS wire Armoured | MTR | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
9 | SCADA Hardware and Software for 200MW | # |  | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
10 | SCADA Hardware and Software for 200MW @ MCR | # |  | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
H2 | Master Control Room | [7 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
1 | Telecommunication Infrastructure | Unit | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
2 | Control Cables (AC and DC), communication cables | Unit | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
3 | Forecasting & Scheduling Software | Unit | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
4 | HVAC | Unit | [6 empty] | 0 | 0 | 0 | 0 | 0 | 12.36% |  | 0 | 0 | 0 | 0 | 0
I | Building and Civil Infrastructure
I1 | MCR, Offices
1 | Master Control Room (MCR) | Rs Lakh | 676 | 15582 | 105.3343 | 14.5361 | 119.8705 |  | 0.04 | 0.01 | 0.05 | 0.0066 | 0.0566 | 13.8% |  | 89.5342 | 12.6401 | 102.1743 | 14.5361 | 119.8705
2 | Offices | Rs Lakh | 676 | 20000 | 135.2 | 18.6576 | 153.8576 |  | 0.05 | 0.01 | 0.06 | 0.0078 | 0.0678 | 13.8% |  | 114.92 | 16.224 | 131.144 | 18.6576 | 153.8576
3 | Housing | Rs Lakh | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
4 | Common Infrastructure | Rs Lakh | 676 | 10000 | 67.6 | 9.3288 | 76.9288 |  | 0.02 | 0 | 0.02 | 0.0024 | 0.0224 | 13.8% |  | 57.46 | 8.112 | 65.572 | 9.3288 | 76.9288
5 | Medical facilities | Rs Lakh | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
I2 | Marine Infrastructure
1 | Pier | Rs Lakh | 2000000 | 1 | 20 | 2.76 | 22.76 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 | 13.8% |  | 17 | 2.4 | 19.4 | 2.76 | 22.76
2 | Ferro Cement Launching Pads | Rs Lakh | 5000000 | 4 | 200 | 27.6 | 227.6 |  | 0.07 | 0.01 | 0.08 | 0.0102 | 0.0902 | 13.8% |  | 170 | 24 | 194 | 27.6 | 227.6
2 | Launch Pads | Rs Lakh | 1000000 | 6 | 60 | 8.28 | 68.28 |  | 0.02 | 0 | 0.02 | 0.0024 | 0.0224 | 13.8% |  | 51 | 7.2 | 58.2 | 8.28 | 68.28
I3 | Other Infrastructure
1 | Lighting | Rs Lakh | 3000 | 2000 | 60 | 8.28 | 68.28 |  | 0.02 | 0 | 0.02 | 0.0024 | 0.0224 | 13.8% |  | 51 | 7.2 | 58.2 | 8.28 | 68.28
2 | Drainage System | Rs Lakh | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
3 | Fencing | Rs Lakh | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
2 | Gates | Rs Lakh | 500000 | 1 | 5 | 0.69 | 5.69 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 4.25 | 0.6 | 4.85 | 0.69 | 5.69
5 | Waste disposal & liquid sewage treatment plant | Rs Lakh | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
6 | Solid waste collection, recycling and storage | Rs Lakh | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
3 | Green Belt | Rs Lakh | 1000000 | 1 | 10 | 1.38 | 11.38 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 8.5 | 1.2 | 9.7 | 1.38 | 11.38
I4 | Environmental Mitigation Charges
| Environment Mitigation Charges | Rs Lakh |  |  | 1000 | 138 | 1138 | 14 | 0.35 | 0.06 | 0.41 | 0.0528 | 0.4628 | 13.8% |  | 0.35 | 0.06 | 0.41 | 0.0528 | 0.4628
J | Other Costs - FPV
1 | Survey, Studies, Design, Approvals | % | 0.15% | 8135252676.8799 | 122.0288 | 16.84 | 138.8688 |  | 0.04 | 0.01 | 0.05 | 0.0066 | 0.0566 | 13.8% |  | 103.7245 | 14.6435 | 118.3679 | 16.84 | 138.8688
2 | Erection Works, Overheads | % | 0.15% | 11693288751.8597 | 175.3993 | 24.2051 | 199.6044 |  | 0.06 | 0.01 | 0.07 | 0.009 | 0.079 | 13.8% |  | 149.0894 | 21.0479 | 170.1374 | 24.2051 | 199.6044
2 | Warranty Costs | % |  | 8135252676.8799 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13.8% |  | 0 | 0 | 0 | 0 | 0
2 | Insurance | % | 0.25% | 8135252676.8799 | 203.3813 | 28.0666 | 231.4479 |  | 0.07 | 0.01 | 0.08 | 0.0102 | 0.0902 | 13.8% |  | 172.8741 | 24.4058 | 197.2799 | 28.0666 | 231.4479
3 | Contingency | % | 3% | 8135252676.8799 | 2440.5758 | 336.7995 | 2777.3753 |  | 0.85 | 0.15 | 1 | 0.129 | 1.129 | 13.8% |  | 2074.4894 | 292.8691 | 2367.3585 | 336.7995 | 2777.3753
4 | Profit Margin | % | 8% | 8135252676.8799 | 6508.2021 | 898.1319 | 7406.334 |  | 2.27 | 0.4 | 2.67 | 0.3444 | 3.0144 | 13.8% |  | 5531.9718 | 780.9843 | 6312.9561 | 898.1319 | 7406.334
F | Optional | [17 empty] | 0 | 0 | 0 | 0 | 0
1 | Differential protection CTs (Supply) & Oil filtration incl. Transit (Service) | Nos | 40000 | 22 | 8.8 | 1.2144 | 10.0144 |  | 0 | 0 | 0 | 0 | 0 |  | 3.6082e-07 | 4.1061e-07 | 13.8% |  | 7.48 | 1.056 | 8.536 | 1.2144 | 10.0144
2 | Telecommunication Infrastructure | Unit | 20000000 | 2 | 400 | 55.2 | 455.2 |  | 0.14 | 0.02 | 0.16 | 0.0204 | 0.1804 |  | 1.6401e-05 | 1.8664e-05 | 13.8% |  | 340 | 48 | 388 | 55.2 | 455.2
3 | PMC Support (fixed duratiobn 10-12 month basis based upto commissioning of the plant) | Lot | 20000000 | 1 | 200 | 27.6 | 227.6 |  | 0.07 | 0.01 | 0.08 | 0.0102 | 0.0902 |  | 8.2005e-06 | 9.3322e-06 | 13.8% |  | 170 | 24 | 194 | 27.6 | 227.6
4 | Means of Coneyence system on water bodies during operation & maintenance phase | Lot | 2000000 | 1 | 20 | 2.76 | 22.76 |  | 0.01 | 0 | 0.01 | 0.0012 | 0.0112 |  | 8.2005e-07 | 9.3322e-07 | 13.8% |  | 17 | 2.4 | 19.4 | 2.76 | 22.76
5 | Wave protection devices (additional protection layer in case of any unforeseen dynamic water forces) | lot | 1000000 | 1 | 10 | 1.38 | 11.38 |  | 0 | 0 | 0 | 0 | 0 |  | 4.1002e-07 | 4.6661e-07 | 13.8% |  | 8.5 | 1.2 | 9.7 | 1.38 | 11.38

## BOQ_T
Transmission Line and Sub-station
Summary | Particulars | Unit Price | Quantity | Unit Rate (Rs Lakhs) | Base Cost | Tax | Lumpsum Cost
| Pooling Sub-Station - 300 MW, 33/220 KV |  |  |  | INR Lakhs | INR Lakhs | INR Lakhs | Equipment Cost | Installation Cost | Base Cost
1 | 33/220 kV, 80 MVA Power Transformer | Lakhs/# | 4 | 1321.984 | 5287.936 | 951.8285 | 6239.7645 | 4494.7456 | 634.5523 | 5129.2979
2 | 33kV Incomer Feeder Bays (25MW) to 33 kV Bus | Lakhs/# | 12 | 20.534 | 246.408 | 44.3534 | 290.7614 | 209.4468 | 29.569 | 239.0158
3 | 33 kV Bus Section & Bus Coupler Bays | Lakhs/# | 8 | 13.0231 | 104.185 | 18.7533 | 122.9383 | 88.5572 | 12.5022 | 101.0594
4 | 33kV incoming feeders for Power transformer | Lakhs/# | 4 | 19.83 | 79.32 | 14.2776 | 93.5976 | 67.422 | 9.5184 | 76.9404
5 | Reactive Power Compensation as per CEA connectivity standard, | Lakhs/MVAr | 60 | 20.5915 | 1235.49 | 222.3882 | 1457.8782 | 1050.1665 | 148.2588 | 1198.4253
6 | 220kV Power Transformer Bay | Lakhs/# | 4 | 41.548 | 166.192 | 29.9146 | 196.1066 | 141.2632 | 19.943 | 161.2062
7 | 220 kV Line Bay+ Bus Coupler Bay | Lakhs/# | 3 | 41.548 | 124.644 | 22.4359 | 147.0799 | 105.9474 | 14.9573 | 120.9047
8 | 220 kV Bus Transfer Bay | Lakhs/# | 1 | 41.548 | 41.548 | 7.4786 | 49.0266 | 35.3158 | 4.9858 | 40.3016
9 | Control & Communication | Lakhs/# | 1 | 408.01 | 408.01 | 73.4418 | 481.4518 | 346.8085 | 48.9612 | 395.7697
A | Pooling Sub-station | MVA | 320 | 24.0429 | 7693.733 | 1384.8719 | 9078.6049 | 6539.673 | 923.248 | 7462.921
Transmission Line
Transmission Line Supply of Material as per specifications
1 | Supply of 220kV Towers including fasteners | Lakhs/Lot | 4 |  | 165.3279 | 29.759 | 195.087 | 140.5287 | 19.8394 | 160.3681
2 | ACCC Conductor, Earthwire Conductor & Accessories | Lakhs/Lot | 4 |  | 481.4585 | 86.6625 | 568.121 | 409.2397 | 57.775 | 467.0147
3 | 220 KV Insulator with Stringing Accessories | Lakhs/Lot | 4 |  | 15.8712 | 2.8568 | 18.728 | 13.4905 | 1.9045 | 15.3951
4 | 220kV Tower Earthing | Lakhs/Lot | 4 |  | 1.6128 | 0.2903 | 1.9031 | 1.3709 | 0.19354 | 1.5644
5 | 220kV Tower Accessories | Lakhs/Lot | 4 |  | 1.5394 | 0.2771 | 1.8165 | 1.3085 | 0.18473 | 1.4932
Transmission Line Services & Erection Activities
1 | Survey and Field Assessment | Lakhs/Lot |  |  | 2.232 | 0.40176 | 2.6338 | 1.8972 | 0.26784 | 2.165
2 | Tower Foundation and Errection | Lakhs/Lot |  |  | 160.0138 | 28.8025 | 188.8163 | 136.0117 | 19.2017 | 155.2134
3 | Mounting of Insulators and Stringing | Lakhs/Lot |  |  | 31.76 | 5.7168 | 37.4768 | 26.996 | 3.8112 | 30.8072
4 | Earthing of transmission towers: | Lakhs/Lot |  |  | 0.84 | 0.1512 | 0.9912 | 0.714 | 0.1008 | 0.8148
5 | ROW / Crop & Land Compensation | Lakhs/Lot |  |  | 106.8 | 19.224 | 126.024 | 90.78 | 12.816 | 103.596
6 | Centage charges | Lakhs/Lot |  |  | 33.2905 | 5.9923 | 39.2828 | 28.2969 | 3.9949 | 32.2918
7 | Erection Charges | Lakhs/Lot |  |  | 130.097 | 23.4175 | 153.5145 | 110.5825 | 15.6116 | 126.1941
B | Transmission Line System |  | 1 | 1130.8432 | 1130.8432 | 203.5518 | 1334.3949 | 961.2167 | 135.7012 | 1096.9179
Augmentation Work @ BkTPS Substation
1 | 220 kV Line Bay+ Bus Section Bay | Lakhs/Lot | 2 | 42.778 | 85.556 | 15.4001 | 100.9561 | 72.7226 | 10.2667 | 82.9893 |  |  |  | 85.556
2 | EHV Cabling | Lakhs/Mtr | 300 | 0.64764 | 194.292 | 34.9726 | 229.2646 | 165.1482 | 23.315 | 188.4632 |  |  |  | 194.292
3 | Miscellaneous (Control and Protection) | Lakhs/No. | 1 | 142.2195 | 142.2195 | 25.5995 | 167.819 | 120.8866 | 17.0663 | 137.9529 |  |  |  | 142.2195
C | Augmentation Works | Lot | 1 | 422.0675 | 422.0675 | 75.9721 | 498.0396 | 358.7574 | 50.6481 | 409.4055
Other Costs
Contingency
1 | Pooling Sub-Station - 300 MW, 33/220 KV |  | 9078.6049 | 3% | 272.3581 | 49.0245 | 321.3826 | 231.5044 | 40.8537 | 272.3581
2 | Transmission Line |  | 1334.3949 | 3% | 40.0318 | 7.2057 | 47.2376 | 34.0271 | 6.0048 | 40.0318
3 | Augmentation Work @ BkTPS Substation |  | 498.0396 | 3% | 14.9412 | 2.6894 | 17.6306 | 12.7 | 2.2412 | 14.9412
D | Contingency |  | 1 | 327.3312 | 327.3312 | 58.9196 | 386.2508 | 278.2315 | 49.0997 | 327.3312
| Grand Total |  |  |  | 9573.9748 | 1723.3155 | 11297.2903 | 8137.8786 | 1158.6969 | 9296.5755
| Transmission Line (220 kV) - BOQ |  | No of Units | Unit Rate | Rs Lakhs
| Transmission Line - Hardware | [5 empty] | 3163.6261
1 | Supply of 220kV Towers including fasteners | Unit
| Type A - Suspension Tower - 00 to 20 | MT | 54.6 | 119400 | 65.1924
| Type B - Double Suspension Tower- 20 to 150 | MT | 18.72 | 119400 | 22.3517
| Type C - Tension Tower - 150 to 300 | MT | 11.232 | 119400 | 13.411
| Type D - Dead End Tower - 300 to 600 | MT | 53.9136 | 119400 | 64.3728
2 | ACCC Conductor, Earthwire Conductor & Accessories | Unit
A | ACCC Zebra Conductor Equivalent
| ACCC Zebra Conductor Equivalent | km | 25.2 | 1368200 | 344.7864
B | Earthwire Conductor
| OPGW Earth Wire (24 Fibers) | km | 8.4 | 139920 | 11.7533
C | ACCC Conductor Hardwares & Accessories
Hardware
| Single Suspension Hardware with AGS Assembly for Zebra Eq. ACCC Conductor | # | 42 | 15630 | 6.5646
| Double Suspension Hardware with AGS Assembly for Zebra Eq. ACCC Conductor | # | 24 | 15630 | 3.7512
| Single Tention Hardware for Zebra Eq. ACCC Conductor | # | 18 | 56580 | 10.1844
| Double Tention Hardware for Zebra Eq. ACCC Conductor | # | 120 | 67940 | 81.528
Accessories
| Mid span compression Joints suitable for ACCC Zebra Conductor Eq. | # | 28 | 58100 | 16.268
| Repairing Sleeve suitable for ACCC Zebra Conductor Eq. | # | 12.6 | 4170 | 0.52542
| Vibration Damper suitable for ACCC Zebra Conductor Eq. | # | 78 | 5740 | 4.4772
| PI Clamp for for ACCC Zebra Conductor Eq. | # | 54 | 1800 | 0.972
| Jumper cone - for each jumper in case of tention tower | # | 30 | 2160 | 0.648
3 | 220 KV Insulator with Stringing Accessories
A | 220 KV, 120 KN polymer Insulators
| 120/160 KN Polymer Insulators | Set | 204 | 7780 | 15.8712
4 | 220kV Tower Earthing
A | Earthing of of 220kV Double Ckt Tower comprising of 3 meter long ISI marked B class 40 MM Dia GI Pipe along with GI Flat 50 X 6 mm | Set | 56 | 2880 | 1.6128
5 | 220kV Tower Accessories
A | Number Plate | # | 56 | 300 | 0.168
B | Danger Plate | # | 56 | 300 | 0.168
C | Circuit Plate | Set | 14 | 300 | 0.042
D | Phase Plate | Set | 14 | 300 | 0.042
E | Bird Guard | Set | 14 | 2200 | 0.308
F | Anti Climbing Devices | Set |  | 0 | 0
G | Tangent Towers incl. contingencies | Set | 7 | 4508 | 0.31556
H | Small Angle Towers incl. contingencies | Set | 2 | 6011.05 | 0.12022
I | Medium Angle Towers incl. contingencies | Set | 1 | 7512.95 | 0.07513
J | Large Angle and Dead End Towers incl. contingencies | Set | 4 | 7512.95 | 0.30052
Transmission Line - Services & Erection
1 | Survey and Field Assessment
A | Preliminary Survey with GPS survey, theodilite & total station, marking route on topo sheets represents actual field conditions | km | 4 | 13700 | 0.548
B | Detailed Survey with GPS, total stations, Digital theodolite etc., along the approved alignments preparation of profiles, tower spotting, tower schedules and soil resistivity | km | 4 | 26600 | 1.064
C | Check Survey, peg marking the tower positions on ground, conforming to the approved Profile and tower schedules using GPS, Total stations, Digital theodolites etc. | km | 4 | 15500 | 0.62
2 | Tower Foundation and Errection
A | Setting with stub for all types of towers with stub setting template which includes erection of stubs, fixing of jacks for supporting template, alignment and leveling excluding cost of excavation and concrete (excluding transportation charges) | Set | 14 | 10300 | 1.442
B | Foundation Cost for 220kV Double Ckt Tower including excavation, cement, reinforcement etc
| Type A - Suspension Tower - 00 to 20 | # | 7 | 800000 | 56
| Type B - Double Suspension Tower - 20 to 150 | # | 2 | 920000 | 18.4
| Type C - Tension Tower - 150 to 300 | # | 1 | 1058000 | 10.58
| Type D - Dead End Tower - 300 to 600 | # | 4 | 1216700 | 48.668
C | Super structure erection of all type of towers including extensions except RC towers including fitting of step bolts, danger plates, number plates, phase plates, circuit plates, bird guards, anti-climbing devices etc. | MT | 138.4656 | 18000 | 24.9238
Mounting of Insulators and Stringing
A | Mounting of Insulators and stringing of single circuit with ACCC Zebra Conductor including laying, jointing, tensioning, sagging clamping and fixing spacers (excluding transportation charges). | km | 4 | 729000 | 29.16
B | Stringing of one (1) no. OPGW earthwire, including laying jointing, tensioning etc., with necessary accessories (excluding transportation charges). | km | 4 | 65000 | 2.6
Earthing of transmission towers:
A | Pipe type earthing including cost of BH coke & salt but excluding cost of earthing set | set | 14 | 6000 | 0.84
ROW / Crop & Land Compensation
A | RoW/Crop Compensation etc | Km | 4 | 800000 | 32
B | Land Compensation for Tower Base | per Tower | 14 | 60000 | 8.4
C | Land Compensation for ROW of the line | per Tower | 14 | 260000 | 36.4
D | Railway Block Charges ( 3 Hours) | Lumsum | 1 | 3000000 | 30
Other Charges
| Centage charges on Total cost of Supply | % |  | 5% | 33.2905
| Labour & Equipment Handling charges | % |  | 8% | 80.0597
| Supervision & Quality Control Charges | % |  | 5% | 50.0373
| Pooling Substation (33/220 kV ) - BOQ | [6 empty] | Ex Works | Erection, Testing, Commissioning @ 20% | Transport Charges @ 5% | Insurance & Labour Cess @ 2% | Supervision, Quality and Margin @ 13% | GST @ 0% | Total
[12 empty] | 0% | 0%
Pooling Sub-station
1 | 33/220 kV, 80 MVA Power Transformer | No.
| Supplying 80 MVA, 3 phase, 50 Hz, oil immersed and ONAN/ ONAF cooling, OLTC, outdoor type, copper wound transformer with delta connection on HV side & Star connection on LV side with additional neutral brought out on load side, voltage rating 220/33 KV with HV tapping of ±10% in step of 1.25% each continuously rated for full load with first filling of oil and standard accessories complete with Test Certificate with Full Load and No load losses limited to the values as per IS 2026 with ISO 9001:2000 certified Nitrogen injection Fire protection system with sump pit, Nitrogen cylinders pipeline & transformer modifications (if required) | No. | 4 | 1321.984 | 5287.936 |  |  | 944.2746 | 188.8549 | 47.2137 | 18.8855 | 122.7557 | 0 | 5287.9376
2 | 33kV Incomer Feeder Bays (25MW) to 33 kV Bus | No.
a | Circuit Breakers
| 36kV Rated voltage, 3 Ph, 50 Hz, triple pole ,outdoor type ,Vacuum Circuit Breaker, rated short circuit breaking current 25 kA for 3 sec., spring mechanism, breaker operation & protection circuit with 110VDC, with supporting structure & necessary equipment etc complete for rated normal current of 1250A | No. | 12 | 4.844 | 58.128 |  |  | 3.4602 | 0.69205 | 0.17301 | 0.069205 | 0.44983 | 0 | 58.1322
b | Lightening Arrestor
| 36 kV, 10 KA, BIL 650 kVp, single phase 50 Hz, station class, gapless type, outdoor, Lightening arrester along with surge counter. | No. | 36 | 0.427 | 15.372 |  |  | 0.305 | 0.061 | 0.01525 | 0.0061 | 0.03965 | 0 | 15.372
c | Isolator
| 36 kV, 3 Phase ,50 HZ, 40 kA, BIL 170 kVp, outdoor, Turn and twist type, centre break isolator with earth switch, supporting structures & other accessories complete . | No. | 36 | 2.688 | 96.768 |  |  | 1.9199 | 0.38398 | 0.095996 | 0.038398 | 0.24959 | 0 | 96.7635
d | Current Transformer
| Single phase 36 kV, 30 VA, 50 HZ, 25kA, BIL 170 kVp, outdoor, 3 core current transformer for line circuit breaker complete with accuracy class Core 1‐0.2 and other cores 5P20 ,with all other necessary accessories -( 400/ 1‐1‐1 A) | No. | 36 | 1.143 | 41.148 |  |  | 0.81675 | 0.16335 | 0.040837 | 0.016335 | 0.10618 | 0 | 41.1642
e | Potential Transformer
| Single phase, 33 kV, 50 Hz, 40 kA, BIL ‐ 170 kVp, 2 core, hermetically sealed, Class F ,outdoor voltage transformer having voltage ratio.145/√3 kV / 110 / √3 V, Accuracy class 0.5 and 3 P respectively & having burden 100 VA | No. | 36 | 0.88 | 31.68 |  |  | 0.62838 | 0.12568 | 0.031419 | 0.012568 | 0.081689 | 0 | 31.6704
f | Cable Termination Kit & Structure
| 33KV, HT Cable outdoor termination kit suitable for XLPE cable (HS type) + Structure Cost | No. | 36 | 0.092 | 3.312 |  |  | 0.066 | 0.0132 | 0.0033 | 0.00132 | 0.00858 | 0 | 3.3264
3 | 33kV Bus Section & Bus Coupler Bays | No.
a | Circuit Breakers
| 36kV Rated voltage, 3 Ph, 50 Hz, triple pole ,outdoor type ,Vacuum Circuit Breaker, rated short circuit breaking current 25 kA for 3 sec., spring mechanism, breaker operation & protection circuit with 110VDC, with supporting structure & necessary equipment etc complete for rated normal current of 1250A | No. | 8 | 4.844 | 38.752 |  |  | 3.4602 | 0.69205 | 0.17301 | 0.069205 | 0.44983 | 0 | 38.7548
b | Isolator
| 36 kV, 3 Phase ,50 HZ, 40 kA, BIL 170 kVp, outdoor, Turn and twist type, centre break isolator with earth switch, supporting structures & other accessories complete . | No. | 16 | 2.688 | 43.008 |  |  | 1.9199 | 0.38398 | 0.095996 | 0.038398 | 0.24959 | 0 | 43.006
c | Current Transformer
| Single phase 36 kV, 30 VA, 50 HZ, 25kA, BIL 170 kVp, outdoor, 3 core current transformer for line circuit breaker complete with accuracy class Core 1‐0.2 and other cores 5P20 ,with all other necessary accessories -( 400/ 1‐1‐1 A) | No. | 15 | 1.143 | 17.145 |  |  | 0.81675 | 0.16335 | 0.040837 | 0.016335 | 0.10618 | 0 | 17.1517
d | Potential Transformer
| Single phase, 33 kV, 50 Hz, 40 kA, BIL ‐ 170 kVp, 2 core, hermetically sealed, Class F ,outdoor voltage transformer having voltage ratio.145/√3 kV / 110 / √3 V, Accuracy class 0.5 and 3 P respectively & having burden 100 VA | No. | 6 | 0.88 | 5.28 |  |  | 0.62838 | 0.12568 | 0.031419 | 0.012568 | 0.081689 | 0 | 5.2784
4 | 33kV incoming feeders for Power transformer | No. | [11 empty] | 79.3257
a | Circuit Breakers
| 36kV Rated voltage, 3 Ph, 50 Hz, triple pole ,outdoor type ,Vacuum Circuit Breaker, rated short circuit breaking current 25 kA for 3 sec., spring mechanism, breaker operation & protection circuit with 110VDC, with supporting structure & necessary equipment etc complete for rated normal current of 2500A | No. | 4 | 5.74 | 22.96 |  |  | 4.1 | 0.82 | 0.205 | 0.082 | 0.533 | 0 | 22.96
b | Isolator
| 36 kV, 3 Phase ,50 HZ, 40 kA, BIL 170 kVp, outdoor, Turn and twist type, centre break isolator with earth switch, supporting structures & other accessories complete . | No. | 4 | 8.795 | 35.18 |  |  | 6.2825 | 1.2565 | 0.31412 | 0.12565 | 0.81672 | 0 | 35.1819
c | Current Transformer
| Single phase 36 kV, 30 VA, 50 HZ, 25kA, BIL 170 kVp, outdoor, 3 core current transformer for line circuit breaker complete with accuracy class Core 1‐0.2 and other cores 5P20 ,with all other necessary accessories -( 750/ 1‐1‐1 A) | No. | 12 | 1.338 | 16.056 |  |  | 0.95594 | 0.19119 | 0.047797 | 0.019119 | 0.12427 | 0 | 16.0598
d | Lightening Arrestor
| 36 kV, 10 KA, BIL 650 kVp, single phase 50 Hz, station class, gapless type, outdoor, Lightening arrester along with surge counter. | No. | 12 | 0.427 | 5.124 |  |  | 0.305 | 0.061 | 0.01525 | 0.0061 | 0.03965 | 0 | 5.124
5 | Reactive Power Compensation | MVAr
A | 33kV Bays for STATCOM | No. | 3 | 0 | 0
a | Circuit Breakers
| 36kV Rated voltage, 3 Ph, 50 Hz, triple pole ,outdoor type ,Vacuum Circuit Breaker, rated short circuit breaking current 25 kA for 3 sec., spring mechanism, breaker operation & protection circuit with 110VDC, with supporting structure & necessary equipment etc complete for rated normal current of 2500A | No. | 3 | 5.74 | 17.22 |  |  | 4.1 | 0.82 | 0.205 | 0.082 | 0.533 | 0 | 17.22
b | Isolator
| 36 kV, 3 Phase ,50 HZ, 40 kA, BIL 170 kVp, outdoor, Turn and twist type, centre break isolator with earth switch, supporting structures & other accessories complete . | No. | 3 | 8.795 | 26.385 |  |  | 6.2825 | 1.2565 | 0.31412 | 0.12565 | 0.81672 | 0 | 26.3865
c | Current Transformer
| Single phase 36 kV, 30 VA, 50 HZ, 25kA, BIL 170 kVp, outdoor, 3 core current transformer for line circuit breaker complete with accuracy class Core 1‐0.2 and other cores 5P20 ,with all other necessary accessories -( 750/ 1‐1‐1 A) | No. | 9 | 1.338 | 12.042 |  |  | 0.95594 | 0.19119 | 0.047797 | 0.019119 | 0.12427 | 0 | 12.0448
d | Lightening Arrestor
| 36 kV, 10 KA, BIL 650 kVp, single phase 50 Hz, station class, gapless type, outdoor, Lightening arrester along with surge counter. | No. | 9 | 0.427 | 3.843 |  |  | 0.305 | 0.061 | 0.01525 | 0.0061 | 0.03965 | 0 | 3.843
B | Installation of STATCOM for Reactive Power Compensation at 33 kV
| According to CEA connectivity standard, to provide dynamic variable reactive power support while maintaining 100% active power and 33% of reactive power at the point of interconnection | MVAr | 60 | 19.6 | 1176 |  |  | 14 | 2.8 | 0.7 | 0.28 | 1.82 | 0 | 1176
6,7,8 | 220kV Bays for Power Transformer, Bus Section , Lines | No.
a | Circuit Breakers
| 245 kV Rated voltage, 3 Ph, 50 Hz, triple pole ,outdoor type , SF6 Circuit Breaker, rated short circuit breaking current 40 kA for 1 sec., spring mechanism, breaker operation & protection circuit with 220VDC/110VDC, with supporting structure & necessary equipment etc complete for rated normal current of 1600 A | No. | 8 | 21.397 | 171.176 |  |  | 15.2833 | 3.0567 | 0.76417 | 0.30567 | 1.9868 | 0 | 171.1733
b | Lightening Arrestor
| 245 kV, 10 KA, BIL 650 kVp, single phase 50 Hz, station class, gapless type, outdoor, Lightening arrester along with surge counter. | No. | 18 | 2.007 | 36.126 |  |  | 1.4333 | 0.28666 | 0.071666 | 0.028666 | 0.18633 | 0 | 36.1197
c | Isolator
| 245 kV, 3 Phase ,50 HZ, 50 kA, BIL 1050 kVp, outdoor, Horizontal centre break type isolator and Horizontal Centre rotating Double Break type isolator shall be gang operated through motor from local as well as from remote control panel. There should be provision for mechanical operation by hand of isolator locally. Earth Switch shall be provided on the line side of the isolator and shall be gang operated mechanically by hand | No. | 30 | 3.007 | 90.21 |  |  | 2.1475 | 0.4295 | 0.10738 | 0.04295 | 0.27918 | 0 | 90.1954
d | Current Transformer
| Single phase 245 kV, 40 VA, 50 HZ, 50 kA, BIL 1050 kVp, outdoor, 5core current transformer for line circuit breaker complete with accuracy class core 1‐0.2 and other cores 5P20 ,with all other necessary accessories. ( 400 /1‐ 1‐1‐1‐1 A) | No. | 24 | 1.233 | 29.592 |  |  | 0.88066 | 0.17613 | 0.044033 | 0.017613 | 0.11449 | 0 | 29.5902
e | Potential Transformer
| Single phase, 220 kV, 50 Hz, 50 kA, BIL 1050 kVp, 3 core, hermetically sealed, Class F ,outdoor voltage transformer having voltage ratio. 220/√3 kV / 110 / √3 V, Accuracy class 0.5 and 3 P respectively & having burden 100 VA | No. | 6 | 0.88 | 5.28 |  |  | 0.62838 | 0.12568 | 0.031419 | 0.012568 | 0.081689 | 0 | 5.2784
9 | Control & Communication | No.
a | Battery
| Supplying Dry type Maintenance free batteries along with all necessary accessories. (Such as cell inter connectors, centre zero 3‐0‐3 Volt DC. voltmeter, mounting rack/stand etc. complete.) all conforming to relevant latest IS. ( 110 cells, 2.0 volts. each, total 220 VDC,300 AH. Capacity ) | No. | 2 | 21.56 | 43.12 |  |  | 15.4 | 3.08 | 0.77 | 0.308 | 2.002 | 0 | 43.12
b | Battery Charger
| Supplying float cum boost Battery charger 3 phase,415 VAC (+/‐ 10 %),50 Hz (+/‐ 5%.) ,Ambient temp. up to 500 c., for following battery voltages and AH ratings. along with all necessary accessories ( such as transformer, rectifier, electronic circuit, circuit breaker, meters, selector switches etc.) conforming to relevant Indian Standards. For Dry type Maintenance free Battery. (20 V,300 AH ) | No. | 2 | 12.366 | 24.732 |  |  | 8.833 | 1.7666 | 0.44165 | 0.17666 | 1.1483 | 0 | 24.7324
c | D.C.Distrubution Boards.(D.C.D.B.)
| 220 V DCDB having one incoming double pole MCB of suitable capacity & 10 nos.16 amps and 5 nos.32 amp. Outgoing feeder with MCB | No. | 96 | 3.031 | 290.976 |  |  | 2.165 | 0.433 | 0.10825 | 0.0433 | 0.28145 | 0 | 290.976
d | Relays
i | Transformer Differential Relay 87‐T, Numerical Type, control voltage 110/220 V DC aux. Supply, flush mounting as per IS 3231. | No. | 4 | 2.202 | 8.808 |  |  | 1.573 | 0.3146 | 0.07865 | 0.03146 | 0.20449 | 0 | 8.8088
ii | Over Current & Earth Fault Relay of approved make combinbed 3 phase over current + 1 earth fault relay (50+51 RYBN) non directional protection, with high set instantaneous trip features 1 Amp, 220/110 V DC aux. Supply etc. complete. | No. | 12 | 0.932 | 11.184 |  |  | 0.6655 | 0.1331 | 0.033275 | 0.01331 | 0.086515 | 0 | 11.1804
iii | Numerical Restricted Earth Fault Relay of approved make with high set instantaneous trip features 1 Amp, 220/110 V DC aux. Supply along with control wiring etc complete | No. | 12 | 1.282 | 15.384 |  |  | 0.9155 | 0.1831 | 0.045775 | 0.01831 | 0.11901 | 0 | 15.3804
iv | Numerical High Speed Trip Relay of approved make with high set instantaneous trip features 1 Amp, 220/110 V DC aux. Supply along with control wiring etc complete | No. | 12 | 0.07 | 0.84 |  |  | 0.05 | 0.01 | 0.0025 | 0.001 | 0.0065 | 0 | 0.84
v | Trip Supervision Relay of approved make with high set 220/110 V DC aux. Supply along with control wiring etc. complete. | No. | 12 | 0.085 | 1.02 |  |  | 0.061 | 0.0122 | 0.00305 | 0.00122 | 0.00793 | 0 | 1.0248
e | Metering
| Metering Kiosk having facility for measurement and metering with Instrument Transformers of appropriate rating and Class | No. | 3 | 3.538 | 10.614 |  |  | 2.527 | 0.5054 | 0.12635 | 0.05054 | 0.32851 | 0 | 62.0694
| ABT meter having facility for measurement and metering of KW, KVA, RKVA, KWH, RKVAH, M.D.P.F. and frequency etc. with class 2.0 accuracy and C.T. ratio 50/5 Amp. and P.T. Ratio 33000/√‾3/110/√‾3 V with all digital meters | No. | 12 | 0.111 | 1.332 |  |  | 0.07932 | 0.015864 | 0.003966 | 0.0015864 | 0.010312 | 0 | 162.6486
| Augmentation Works - BoQ | [6 empty] | Ex Works Prices ( Supply) | Erection, testing, commissioning charges @ 20% | Transport Charges @ 5% | Insurance & Labour Cess @ 2% | Contingencies with Suopervision and Quality Control@ 13% | GST @ 0% | Total
[12 empty] | 13% | 0%
1 | 220kV Bays for Transmission Lines | No.
a | Circuit Breakers
| 245 kV Rated voltage, 3 Ph, 50 Hz, triple pole ,outdoor type , SF6 Circuit Breaker, rated short circuit breaking current 40 kA for 1 sec., spring mechanism, breaker operation & protection circuit with 220VDC/110VDC, with supporting structure & necessary equipment etc complete for rated normal current of 1600 A | No. | 2 | 21.397 | 42.794 |  |  | 15.2833 | 3.0567 | 0.76417 | 0.30567 | 1.9868 | 0 | 42.7933
b | Lightening Arrestor
| 245 kV, 10 KA, BIL 650 kVp, single phase 50 Hz, station class, gapless type, outdoor, Lightening arrester along with surge counter. | No. | 6 | 2.007 | 12.042 |  |  | 1.4333 | 0.28666 | 0.071666 | 0.028666 | 0.18633 | 0 | 12.0399
c | Isolator
| 245 kV, 3 Phase ,50 HZ, 50 kA, BIL 1050 kVp, outdoor, Horizontal centre break type isolator and Horizontal Centre rotating Double Break type isolator shall be gang operated through motor from local as well as from remote control panel. There should be provision for mechanical operation by hand of isolator locally. Earth Switch shall be provided on the line side of the isolator and shall be gang operated mechanically by hand | No. | 6 | 3.007 | 18.042 |  |  | 2.1475 | 0.4295 | 0.10738 | 0.04295 | 0.27918 | 0 | 18.0391
d | Current Transformer
| Single phase 245 kV, 40 VA, 50 HZ, 50 kA, BIL 1050 kVp, outdoor, 5core current transformer for line circuit breaker complete with accuracy class core 1‐0.2 and other cores 5P20 ,with all other necessary accessories. ( 400 /1‐ 1‐1‐1‐1 A) | No. | 6 | 1.233 | 7.398 |  |  | 0.88066 | 0.17613 | 0.044033 | 0.017613 | 0.11449 | 0 | 7.3975
e | Potential Transformer
| Single phase, 220 kV, 50 Hz, 50 kA, BIL 1050 kVp, 3 core, hermetically sealed, Class F ,outdoor voltage transformer having voltage ratio. 220/√3 kV / 110 / √3 V, Accuracy class 0.5 and 3 P respectively & having burden 100 VA | No. | 6 | 0.88 | 5.28 |  |  | 0.62838 | 0.12568 | 0.031419 | 0.012568 | 0.081689 | 0 | 5.2784
2 | EHV Cabling | mtr
a | 230 kV(), Single Core 1200 Sq. mm. Alumintum conductor XLPE Insulated, Corrugated Aluminium Sheath, Aluminium wire armoured, HOPE outer sheathed power cable | km | 0.9 | 154 | 138.6 |  |  | 110 | 22 | 5.5 | 2.2 | 14.3 | 0 | 138.6
b | 230 kV straight through joint for 230 kV 1C X 1200 Sq.mm XLPE Alu cable | No. | 3 | 5.692 | 17.076 |  |  | 4.0657 | 0.81314 | 0.20329 | 0.081314 | 0.52854 | 0 | 17.076
c | 230 kV outdoor termination kit for 230 kV 1CX1200 Sq.mm XLPE Alu cable | No. | 3 | 12.295 | 36.885 |  |  | 8.782 | 1.7564 | 0.4391 | 0.17564 | 1.1417 | 0 | 36.8845
d | 230 kV outdoor termination structure | No. | 3 | 0.577 | 1.731 |  |  | 0.41221 | 0.082442 | 0.020611 | 0.0082442 | 0.053587 | 0 | 1.7313
3 | Sub Station Modification ( Shifting of existing Equipments etc )
| Sub Station Modification ( Shifting of existing Equipments etc ) | Lump Sum | 1 | 40.217 | 40.217 |  |  | 28.7266 | 5.7453 | 1.4363 | 0.57453 | 3.7345 | 0 | 80.4343
Note on B106: Store incidental charges, contingencies, work contract establishment

## BOQ_I
Transmission Line and Sub-station
Summary | Particulars |  | Unit Rate | Quantity | Base Cost | Tax | Lumpsum Cost | Equipment Cost | Installation Cost
A | Land & Site Development |  |  |  | 1502.05 | 270.369 | 1772.419 | 1276.7425 | 180.246
B | Road Infrastructure |  |  |  | 73.5 | 13.23 | 86.73 | 62.475 | 8.82
| Infrastructure Cost Total |  |  |  | 1575.55 | 283.599 | 1859.149 | 1339.2175 | 189.066
C | Other Charges |  |  |  | 208.24 | 37.4832 | 245.7232 | 177.004 | 24.9888
| Grand Total |  |  |  | 1783.79 | 321.0822 | 2104.8722 | 1516.2215 | 214.0548
| Infrastructure Development | Unit Price | Rate | Quantity | Base Cost | Tax | Total Cost
A | Land
1 | Pooling S/S + Control Room | Rs Lakh/ acre | 0 | 11.125 | 0 | 0 | 0 | 18%
2 | Approach Roads | Rs Lakh/ acre | 0 | 0.6125 | 0 | 0 | 0 | 18%
3 | FSPV Master Control Room | Rs Lakh/ acre | 0 | 3.8955 | 0 | 0 | 0
4 | Storage | Rs Lakh/ acre | 0 | 4.125 | 0 | 0 | 0 | 18%
| Land Total | Rs Lakh |  | 19.758 | 0 | 0 | 0
B | Site Development
1 | Site Development | Rs Lakh | 100 | 15.0205 | 1502.05 | 270.369 | 1772.419 | 18%
2 | Green Belt | Rs Lakh | 0 | 0 | 0 | 0 | 0 | 18%
| Site Development Total |  |  |  | 1502.05 | 270.369 | 1772.419
C | Road Infrastructure
1 | Access Road to Site | Rs Lakh | 120 | 0.6125 | 73.5 | 13.23 | 86.73 | 18%
| Road Infrastructure Total |  |  | 0.6125 | 73.5 | 13.23 | 86.73
Other Charges/Statutory Charges
1 | Local Area Development Charges | Rs Lakh | 100000 | 203.24 | 203.24 | 36.5832 | 239.8232 | 18%
2 | Registration Cost | Rs Lakh | 0 | 203.24 | 0 | 0 | 0 | 18%
3 | Legal Charges | Rs Lakh | 0 | 203.24 | 0 | 0 | 0 | 18%
4 | Regulatory Charges | Rs Lakh | 500000 | 1 | 5 | 0.9 | 5.9 | 18%
| Other Charges - Total | Rs Lakh |  |  | 208.24 | 37.4832 | 245.7232

## Working
| Particulars | Units | Inputs | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057
|  |  | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31 | 2031-03-31 | 2032-03-31 | 2033-03-31 | 2034-03-31 | 2035-03-31 | 2036-03-31 | 2037-03-31 | 2038-03-31 | 2039-03-31 | 2040-03-31 | 2041-03-31 | 2042-03-31 | 2043-03-31 | 2044-03-31 | 2045-03-31 | 2046-03-31 | 2047-03-31 | 2048-03-31 | 2049-03-31 | 2050-03-31 | 2051-03-31 | 2052-03-31 | 2053-03-31 | 2054-03-31 | 2055-03-31 | 2056-03-31 | 2057-03-31
| Total Year Counter |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
| Is Operational ? | 26 |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
| Operational Year Number |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 26 | 26 | 26 | 26 | 26
| Days in year |  |  | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365
| Days of Construction |  |  | 0: 365; 1: 183; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0
| Days in Operations |  |  | 0 | 182 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 183 | 0 | 0 | 0 | 0 | 0
| Proportion of year in operation |  |  | 0 | 0.49863 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
| Cumulative number of year in operation |  |  | 0 | 0.49863 | 1.4986 | 2.4986 | 3.4986 | 4.4986 | 5.4986 | 6.4986 | 7.4986 | 8.4986 | 9.4986 | 10.4986 | 11.4986 | 12.4986 | 13.4986 | 14.4986 | 15.4986 | 16.4986 | 17.4986 | 18.4986 | 19.4986 | 20.4986 | 21.4986 | 22.4986 | 23.4986 | 24.4986 | 24.9986 | 24.9986 | 24.9986 | 24.9986 | 24.9986 | 24.9986
CapEX
| Capacity of the Project | MW | 203.24 | 1: MWp; 2: 243.888
| Generation Project | Unit | Unit Cost | 0: Quantity; 1: Cost (Rs Lakh); 2: Tax; 3: Total Cost
II | Capital Expenditure - Generation | bar: 0 to 3
A | SPV Modules | Lot | 159 | 0: 243.888; 1: 38728.4827; 2: 5344.5306; 3: 44073.0133
B | Inverters | Lot | 13 | 0: 203.24; 1: 2650.5; 2: 365.769; 3: 3016.269
C | Floating Structure for Module and inverters | Lot | 135 | 0: 243.888; 1: 32929.8607; 2: 4544.3208; 3: 37474.1815
D | Balance of Plant (Cables, SCB, Accessories) | Lot | 40 | 0: 243.888; 1: 9694.1833; 2: 1337.7973; 3: 11031.9806
E | Civil Structure | Lot | 7 | 0: 243.888; 1: 1663.1343; 2: 229.5125; 3: 1892.6469
| Capital Expenditure - Generation | Lot |  | 1: 85666.1611; 2: 11821.9302; 3: 97488.0913
III | Capital Expenditure - Transmission Evacuation | bar: 0 to 3
A | Pooling Sub-station | MVA | 24.0429 | 0: 320; 1: 7693.733; 2: 1384.8719; 3: 9078.6049
B | Transmission Line System | kM | 282.7108 | 0: 4; 1: 1130.8432; 2: 203.5518; 3: 1334.3949
C | Augmentation Works | Lot | 422.0675 | 0: 1; 1: 422.0675; 2: 75.9721; 3: 498.0396
| Capital Expenditure - Transmission Evacuation | Lot |  | 1: 9246.6437; 2: 1664.3959; 3: 10911.0395
I | Capital Expenditure - Infrastructure | bar: 0 to 3
A | Land & Site Development | Lot | 0 | 0: 0; 1: 1502.05; 2: 270.369; 3: 1772.419
B | Road Infrastructure | Lot | 0 | 0: 0; 1: 73.5; 2: 13.23; 3: 86.73
| Capital Expenditure - Infrastructure | Lot |  | 1: 1575.55; 2: 283.599; 3: 1859.149
IV | Capital Expenditure - Other Costs | bar: 0 to 3
A | Generation (Contingency, Insurance, Warranty, etc) | Lot |  | 1: 9449.5874; 2: 1304.0431; 3: 10753.6304
B | Transmission (Contingency, Insurance, Warranty, etc) | Lot |  | 1: 327.3312; 2: 58.9196; 3: 386.2508
C | Other Charges/Statutory Charges | Lot |  | 1: 208.24; 2: 37.4832; 3: 245.7232
| Capital Expenditure - Other Costs | Lot |  | 1: 9985.1586; 2: 1400.4459; 3: 11385.6044
| Total Project Cost w/o IDC |  |  | 1: 106473.5133; 2: 15170.371; 3: 121643.8843
| Interest During Construction | Lot |  | 3: 2612.319
| Grand Total | Lot |  | 1: 106473.5133; 2: 15170.371; 3: 124256.2032
Capital Cost without IDC | bar: 0 to 3
1 | Capital Expenditure - Generation & Transmission | Rs Cr |  | 1: 949.128; 2: 134.8633; 3: 1083.9913
2 | Capital Expenditure - Infrastructure | Rs Cr |  | 1: 15.7555; 2: 2.836; 3: 18.5915
3 | Capital Expenditure - Other Costs | Rs Cr |  | 1: 99.8516; 2: 14.0045; 3: 113.856
| Capital Cost - Total | Rs Cr |  | 1: 1064.7351; 2: 151.7037; 3: 1216.4388
| Interest During Construction | Rs Cr |  | 3: 26.1232
| Gross Capital Cost | Rs Cr |  | 3: 1242.562
Phasing
1 | Capital Expenditure - Generation & Transmission | Rs Cr | 1083.9913 | 559.9333 | 524.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital Expenditure - Infrastructure | Rs Cr | 18.5915 | 5.5774 | 13.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Capital Expenditure - Other Costs | Rs Cr | 113.856 | 11.3856 | 102.4704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phasing - Capex | Rs Cr | 1216.4388 | 576.8963 | 639.5425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IDC | Rs Cr | 26.1232 | 5.1523 | 20.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capex incl. IDC | Rs Cr | 1242.562 | 582.0486 | 660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commerical Loan 1 | % |  | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70%
| Commercial Loan 2 | % | bar: 0 to 26
| Grant | % | bar: 0 to 26
| Equity | % |  | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30%
| Commerical Loan 1 | Rs Cr | 869.7934 | 407.434 | 462.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commerical Loan 2 | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grant | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equity | Rs Cr | 372.7686 | 174.6146 | 198.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Grant Schedule
| Grant | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cumulative Grant | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Equity Schedule
| Equity | Rs Cr |  | 174.6146 | 198.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cumulative Equity | Rs Cr |  | 174.6146 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686
Commerical Loan 1 Schedule
| Opening | Rs Cr |  | 0 | 407.434 | 840.8003 | 782.8141 | 724.8279 | 666.8416 | 608.8554 | 550.8692 | 492.8829 | 434.8967 | 376.9105 | 318.9243 | 260.938 | 202.9518 | 144.9656 | 86.9793 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Addition | Rs Cr | 869.7934 | 407.434 | 462.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repayments | Rs Cr |  | 0 | 28.9931 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 407.434 | 840.8003 | 782.8141 | 724.8279 | 666.8416 | 608.8554 | 550.8692 | 492.8829 | 434.8967 | 376.9105 | 318.9243 | 260.938 | 202.9518 | 144.9656 | 86.9793 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Rate | % | bar: 0 to 26
| IDC | Rs Cr |  | 5.1523 | 20.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Charge | Rs Cr | 384.8552 | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commercial Loan 2 Schedule
| Opening | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Addition | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repayments | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Rate | % |  | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
| IDC | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Charge | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GFA & Depreciation Schedule
CWIP Schedule
| Opening | Rs Cr |  | 0 | 582.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Addition | Rs Cr |  | 582.0486 | 660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capitalised | Rs Cr |  | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 582.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book Depreciation |  |  |  | 14: 186.3843
| GFA Schedule |  |  | 14: 393.0397; 15: 335.0121; 16: 276.9844; 17: 252.1332; 18: 227.282; 19: 202.4307; 20: 177.5795; 21: 152.7282
| Opening GFA | Rs Cr |  | 0 | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Additions | Rs Cr | 1242.562 | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr | 1102.2594 | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| Accumulated depreciation | Rs Cr |  | 0 | 28.9343 | 86.962 | 144.9896 | 203.0173 | 261.0449 | 319.0726 | 377.1002 | 435.1279 | 493.1555 | 551.1832 | 609.2108 | 667.2384 | 725.2661 | 783.2937 | 841.3214 | 866.1726 | 891.0239 | 915.8751 | 940.7264 | 965.5776 | 990.4288 | 1015.2801 | 1040.1313 | 1064.9826 | 1089.8338 | 1102.2594 | 1102.2594 | 1102.2594 | 1102.2594 | 1102.2594
| Closing GFA | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Max depreciation | Rs Cr | 88.71% | 0 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058
[18 empty] | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562
| Opening NFA | Rs Cr |  | 0 | 0 | 1213.6277 | 1155.6001 | 1097.5724 | 1039.5448 | 981.5171 | 923.4895 | 865.4618 | 807.4342 | 749.4065 | 691.3789 | 633.3512 | 575.3236 | 517.2959 | 459.2683 | 401.2406 | 376.3894 | 351.5382 | 326.6869 | 301.8357 | 276.9844 | 252.1332 | 227.282 | 202.4307 | 177.5795 | 152.7282 | 140.3026 | 140.3026 | 140.3026 | 140.3026
| Addition - NFA | Rs Cr | 1242.562 | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr | 1102.2594 | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| Closing - NFA | Rs Cr |  | 0 | 1213.6277 | 1155.6001 | 1097.5724 | 1039.5448 | 981.5171 | 923.4895 | 865.4618 | 807.4342 | 749.4065 | 691.3789 | 633.3512 | 575.3236 | 517.2959 | 459.2683 | 401.2406 | 376.3894 | 351.5382 | 326.6869 | 301.8357 | 276.9844 | 252.1332 | 227.282 | 202.4307 | 177.5795 | 152.7282 | 140.3026 | 140.3026 | 140.3026 | 140.3026 | 140.3026
Accumulated Depreciation
| Opening | Rs Cr |  | 0 | 0 | 28.9343 | 86.962 | 144.9896 | 203.0173 | 261.0449 | 319.0726 | 377.1002 | 435.1279 | 493.1555 | 551.1832 | 609.2108 | 667.2384 | 725.2661 | 783.2937 | 841.3214 | 866.1726 | 891.0239 | 915.8751 | 940.7264 | 965.5776 | 990.4288 | 1015.2801 | 1040.1313 | 1064.9826 | 1089.8338 | 1102.2594 | 1102.2594 | 1102.2594 | 1102.2594
| Depreciation during the year | Rs Cr | 1102.2594 | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 0 | 28.9343 | 86.962 | 144.9896 | 203.0173 | 261.0449 | 319.0726 | 377.1002 | 435.1279 | 493.1555 | 551.1832 | 609.2108 | 667.2384 | 725.2661 | 783.2937 | 841.3214 | 866.1726 | 891.0239 | 915.8751 | 940.7264 | 965.5776 | 990.4288 | 1015.2801 | 1040.1313 | 1064.9826 | 1089.8338 | 1102.2594 | 1102.2594 | 1102.2594 | 1102.2594 | 1102.2594
Depreciation (Tax)
GFA Schedule
| Opening GFA | Rs Cr |  | 0 | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Additions | Rs Cr | 1242.562 | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr | 1242.1893 | 0 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accumulated depreciation | Rs Cr |  | 0 | 95.553 | 191.106 | 286.6591 | 382.2121 | 477.7651 | 573.3181 | 668.8711 | 764.4242 | 859.9772 | 955.5302 | 1051.0832 | 1146.6362 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893
| Closing GFA | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Max depreciation | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
Accelerated Depreciation
GFA Schedule
| Opening GFA | Rs Cr |  | 0 | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Additions | Rs Cr | 1242.562 | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr | 1118.3058 | 0 | 0 | 621.281 | 0 | 497.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accumulated depreciation | Rs Cr |  | 0 | 0 | 621.281 | 621.281 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058
| Closing GFA | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Max depreciation | Rs Cr |  | 0 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058
| Opening NFA | Rs Cr |  | 0 | 0 | 1242.562 | 621.281 | 621.281 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562
| Addition - NFA | Rs Cr |  | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 0 | 621.281 | 0 | 497.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing - NFA | Rs Cr |  | 0 | 1242.562 | 621.281 | 621.281 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562 | 124.2562
Accumulated Depreciation
| Opening | Rs Cr |  | 0 | 0 | 0 | 621.281 | 621.281 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058
| Depreciation during the year | Rs Cr |  | 0 | 0 | 621.281 | 0 | 497.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 0 | 0 | 621.281 | 621.281 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058
Benefits of Accelerated Depreciation
| Net Depreciation Benefit | Rs Cr |  | 0 | -28.9343 | 563.2534 | -58.0276 | 438.9972 | -58.0276 | -58.0276 | -58.0276 | -58.0276 | -58.0276 | -58.0276 | -58.0276 | -58.0276 | -58.0276 | -58.0276 | -58.0276 | -24.8512 | -24.8512 | -24.8512 | -24.8512 | -24.8512 | -24.8512 | -24.8512 | -24.8512 | -24.8512 | -24.8512 | -12.4256 | 0 | 0 | 0 | 0
| Tax Rate | % | bar: 0 to 26
| Tax Benefit | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Revenue |  |  |  | 1: 19.01%
| Capacity | MW | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24
| Degradation | % |  | 0% | 0.2493% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.25% | 0% | 0% | 0% | 0%
| Effective capacity | MW | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24
| CUF | % | 19.32% | 0% | 19.26% | 18.91% | 18.72% | 18.49% | 18.26% | 17.98% | 17.8% | 17.58% | 17.36% | 17.1% | 16.93% | 16.72% | 16.51% | 16.26% | 16.1% | 15.9% | 15.7% | 15.46% | 15.31% | 15.12% | 14.93% | 14.7% | 14.56% | 14.37% | 14.19% | 16.47% | 0% | 0% | 0% | 0%
| APC | % |  | 0% | 0.374% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.375% | 0% | 0% | 0% | 0%
| Generation | MU | 343.931 | 0 | 170.9605 | 337.5083 | 333.2894 | 329.1233 | 325.0093 | 320.9467 | 316.9348 | 312.9732 | 309.061 | 305.1977 | 301.3828 | 297.6155 | 293.8953 | 290.2216 | 286.5938 | 283.0114 | 279.4738 | 275.9803 | 272.5306 | 269.1239 | 265.7599 | 262.4379 | 259.1574 | 255.918 | 252.719 | 147.019 | 0 | 0 | 0 | 0
| Tariff | Rs/kWh |  | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536
| Revenue | Rs Cr |  | 0 | 89.815 | 177.3117 | 175.0953 | 172.9066 | 170.7453 | 168.611 | 166.5034 | 164.4221 | 162.3668 | 160.3372 | 158.333 | 156.3538 | 154.3994 | 152.4694 | 150.5635 | 148.6815 | 146.823 | 144.9877 | 143.1753 | 141.3857 | 139.6183 | 137.8731 | 136.1497 | 134.4478 | 132.7672 | 77.2372 | 0 | 0 | 0 | 0
O&M
| Generation O&M | Rs Cr | 566.6227 | 0 | 5.5726 | 11.7625 | 12.38 | 13.03 | 13.714 | 14.434 | 15.1918 | 15.9894 | 16.8288 | 17.7123 | 18.6422 | 19.621 | 20.6511 | 21.7352 | 22.8763 | 24.0773 | 25.3414 | 26.6718 | 28.0721 | 29.5459 | 31.0971 | 32.7296 | 34.448 | 36.2565 | 38.1599 | 20.0817 | 0 | 0 | 0 | 0
1 | Infrastructure O&M
| Lease Rent | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Use charges | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Road, building maintenance | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SLDC Charges | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A&G Charges | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transmission O&M | Rs Cr | 97.9409 | 0 | 1.1878 | 2.4719 | 2.5651 | 2.6618 | 2.7621 | 2.8663 | 2.9743 | 3.0864 | 3.2028 | 3.3235 | 3.4488 | 3.5789 | 3.7138 | 3.8538 | 3.9991 | 4.1499 | 4.3063 | 4.4687 | 4.6371 | 4.8119 | 4.9933 | 5.1816 | 5.3769 | 5.5797 | 5.79 | 2.9491 | 0 | 0 | 0 | 0
| Infrastructure O&M | Rs Cr | 97.9409 | 0 | 1.1878 | 2.4719 | 2.5651 | 2.6618 | 2.7621 | 2.8663 | 2.9743 | 3.0864 | 3.2028 | 3.3235 | 3.4488 | 3.5789 | 3.7138 | 3.8538 | 3.9991 | 4.1499 | 4.3063 | 4.4687 | 4.6371 | 4.8119 | 4.9933 | 5.1816 | 5.3769 | 5.5797 | 5.79 | 2.9491 | 0 | 0 | 0 | 0
| O&M Total | Rs Cr | 664.5635 | 0 | 6.7603 | 14.2344 | 14.9451 | 15.6917 | 16.4762 | 17.3003 | 18.1661 | 19.0758 | 20.0316 | 21.0359 | 22.0911 | 23.1998 | 24.3649 | 25.589 | 26.8754 | 28.2272 | 29.6477 | 31.1405 | 32.7092 | 34.3578 | 36.0904 | 37.9112 | 39.8249 | 41.8361 | 43.9499 | 23.0307 | 0 | 0 | 0 | 0
Interest on Working Capital
| Receivables | Rs Cr |  | 0 | 22.5154 | 22.164 | 21.8869 | 21.6133 | 21.3432 | 21.0764 | 20.8129 | 20.5528 | 20.2958 | 20.0422 | 19.7916 | 19.5442 | 19.2999 | 19.0587 | 18.8204 | 18.5852 | 18.3529 | 18.1235 | 17.8969 | 17.6732 | 17.4523 | 17.2341 | 17.0187 | 16.806 | 16.5959 | 19.3093 | 0 | 0 | 0 | 0
| O&M | Rs Cr |  | 0 | 1.1298 | 1.1862 | 1.2454 | 1.3076 | 1.373 | 1.4417 | 1.5138 | 1.5897 | 1.6693 | 1.753 | 1.8409 | 1.9333 | 2.0304 | 2.1324 | 2.2396 | 2.3523 | 2.4706 | 2.595 | 2.7258 | 2.8632 | 3.0075 | 3.1593 | 3.3187 | 3.4863 | 3.6625 | 3.8385 | 0 | 0 | 0 | 0
| Maintenance spares | Rs Cr |  | 0 | 2.0337 | 2.1352 | 2.2418 | 2.3538 | 2.4714 | 2.595 | 2.7249 | 2.8614 | 3.0047 | 3.1554 | 3.3137 | 3.48 | 3.6547 | 3.8384 | 4.0313 | 4.2341 | 4.4472 | 4.6711 | 4.9064 | 5.1537 | 5.4136 | 5.6867 | 5.9737 | 6.2754 | 6.5925 | 6.9092 | 0 | 0 | 0 | 0
| Total | Rs Cr |  | 0 | 25.6789 | 25.4853 | 25.3741 | 25.2747 | 25.1876 | 25.1131 | 25.0517 | 25.0038 | 24.9699 | 24.9505 | 24.9462 | 24.9575 | 24.9851 | 25.0295 | 25.0914 | 25.1715 | 25.2707 | 25.3896 | 25.5291 | 25.69 | 25.8734 | 26.0801 | 26.3112 | 26.5677 | 26.8509 | 30.057 | 0 | 0 | 0 | 0
| Bank borrowing | Rs Cr |  | 0 | 19.2592 | 19.114 | 19.0306 | 18.9561 | 18.8907 | 18.8348 | 18.7888 | 18.7528 | 18.7274 | 18.7129 | 18.7097 | 18.7181 | 18.7388 | 18.7721 | 18.8185 | 18.8787 | 18.953 | 19.0422 | 19.1468 | 19.2675 | 19.405 | 19.5601 | 19.7334 | 19.9258 | 20.1382 | 22.5427 | 0 | 0 | 0 | 0
| Interest Rate | Rs Cr |  | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5% | 11.5%
| Interest on Working Capital | Rs Cr |  | 0 | 1.1044 | 2.1981 | 2.1885 | 2.1799 | 2.1724 | 2.166 | 2.1607 | 2.1566 | 2.1537 | 2.152 | 2.1516 | 2.1526 | 2.155 | 2.1588 | 2.1641 | 2.171 | 2.1796 | 2.1899 | 2.2019 | 2.2158 | 2.2316 | 2.2494 | 2.2693 | 2.2915 | 2.3159 | 1.2962 | 0 | 0 | 0 | 0
DSRA
Debt Service Requirement
| Interest on Debt | Rs Cr | 384.8552 | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Debt Repayment | Rs Cr | 869.7934 | 0 | 28.9931 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | Rs Cr | 1254.6487 | 0 | 47.6653 | 106.6947 | 103.2155 | 99.7363 | 96.2571 | 92.778 | 89.2988 | 85.8196 | 82.3404 | 78.8613 | 75.3821 | 71.9029 | 68.4237 | 64.9446 | 61.4654 | 29.8629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRA
| Opening | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Additions | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest Income
| Interest Rate | % | bar: 0 to 26
| Interest | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BG Cost
| Interest Rate | % | bar: 0 to 26
| Interest | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ROE
| Cumulative Equity | Rs Cr |  | 174.6146 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686
| Post-Tax RoE | % |  | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14%
| Post-Tax RoE | Rs Cr |  | 0 | 26.0223 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 52.1876 | 26.0938 | 0 | 0 | 0 | 0
| Effective Tax Rate | % |  | 0% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22%
| Pre-Tax RoE | % |  | 14% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 17.95% | 17.95% | 17.95% | 17.95% | 17.95% | 17.95% | 17.95% | 17.95% | 17.95% | 17.95%
| Pre-Tax RoE | Rs Cr |  | 0 | 31.4127 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 66.9072 | 66.9072 | 66.9072 | 66.9072 | 66.9072 | 33.4536 | 0 | 0 | 0 | 0
Cash Deficit Loan Requirement Computation
| Revenue | Rs Cr |  | 0 | 89.815 | 177.3117 | 175.0953 | 172.9066 | 170.7453 | 168.611 | 166.5034 | 164.4221 | 162.3668 | 160.3372 | 158.333 | 156.3538 | 154.3994 | 152.4694 | 150.5635 | 148.6815 | 146.823 | 144.9877 | 143.1753 | 141.3857 | 139.6183 | 137.8731 | 136.1497 | 134.4478 | 132.7672 | 77.2372 | 0 | 0 | 0 | 0
| O&M Expenses | Rs Cr |  | 0 | -6.7603 | -14.2344 | -14.9451 | -15.6917 | -16.4762 | -17.3003 | -18.1661 | -19.0758 | -20.0316 | -21.0359 | -22.0911 | -23.1998 | -24.3649 | -25.589 | -26.8754 | -28.2272 | -29.6477 | -31.1405 | -32.7092 | -34.3578 | -36.0904 | -37.9112 | -39.8249 | -41.8361 | -43.9499 | -23.0307 | 0 | 0 | 0 | 0
| Infrastructure Charges | Rs Cr
| Interest | Rs Cr |  | 0 | -18.6722 | -48.7084 | -45.2293 | -41.7501 | -38.2709 | -34.7917 | -31.3126 | -27.8334 | -24.3542 | -20.875 | -17.3959 | -13.9167 | -10.4375 | -6.9583 | -3.4792 | -0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on WC | Rs Cr |  | 0 | -1.1044 | -2.1981 | -2.1885 | -2.1799 | -2.1724 | -2.166 | -2.1607 | -2.1566 | -2.1537 | -2.152 | -2.1516 | -2.1526 | -2.155 | -2.1588 | -2.1641 | -2.171 | -2.1796 | -2.1899 | -2.2019 | -2.2158 | -2.2316 | -2.2494 | -2.2693 | -2.2915 | -2.3159 | -1.2962 | 0 | 0 | 0 | 0
| Taxes | Rs Cr |  | 0 | -5.8934 | -9.291 | -9.3873 | -9.4821 | -9.575 | -9.6654 | -9.7531 | -9.8376 | -9.9184 | -9.9951 | -10.0672 | -10.1342 | -10.1955 | -10.2506 | -10.2989 | -15.8837 | -15.4688 | -14.8959 | -14.3137 | -14.3619 | -22.2852 | -21.4967 | -20.6922 | -19.8705 | -19.0303 | -11.6403 | 0 | 0 | 0 | 0
| Change in DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Income on DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BG cost for DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Change in WC | Rs Cr |  | 0 | -25.6789 | 0.19361 | 0.11121 | 0.099367 | 0.087135 | 0.074495 | 0.061424 | 0.047898 | 0.033889 | 0.019371 | 0.0043145 | -0.011311 | -0.027536 | -0.044395 | -0.061924 | -0.080158 | -0.099138 | -0.1189 | -0.1395 | -0.16096 | -0.18335 | -0.20671 | -0.23109 | -0.25655 | -0.28315 | -3.2061 | 0 | 0 | 0 | 0
| Change in WC Loan | Rs Cr |  | 0 | 19.2592 | -0.14521 | -0.083411 | -0.074525 | -0.065351 | -0.055871 | -0.046068 | -0.035923 | -0.025417 | -0.014528 | -0.0032359 | 0.0084829 | 0.020652 | 0.033297 | 0.046443 | 0.060119 | 0.074353 | 0.089177 | 0.10462 | 0.12072 | 0.13751 | 0.15503 | 0.17332 | 0.19241 | 0.21236 | 2.4046 | 0 | 0 | 0 | 0
| Capital Expenditure | Rs Cr |  | -582.0486 | -660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grant | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Debt | Rs Cr |  | 407.434 | 462.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Debt Repayment | Rs Cr |  | 0 | -28.9931 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equity | Rs Cr |  | 174.6146 | 198.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on Cash deficit Loan | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repayment of cash deficit loan | Rs Cr
| Cash deficit Loan | Rs Cr
Cash Balance
| Opening | Rs Cr |  | 0 | 2.8422e-14 | 21.9718 | 66.9139 | 112.3006 | 158.1419 | 204.4283 | 251.1482 | 298.2882 | 345.8326 | 393.7638 | 442.0615 | 490.7036 | 539.6651 | 588.9185 | 638.4338 | 688.1779 | 760.6946 | 860.1967 | 956.9284 | 1050.8441 | 1141.254 | 1220.2193 | 1296.3834 | 1369.6889 | 1440.0745 | 1507.4748 | 1547.9433 | 1547.9433 | 1547.9433 | 1547.9433
| Addition | Rs Cr |  | 2.8422e-14 | 21.9718 | 44.942 | 45.3867 | 45.8413 | 46.2864 | 46.7199 | 47.14 | 47.5444 | 47.9311 | 48.2978 | 48.6421 | 48.9615 | 49.2534 | 49.5153 | 49.7442 | 72.5166 | 99.5021 | 96.7317 | 93.9157 | 90.4099 | 78.9653 | 76.164 | 73.3055 | 70.3856 | 67.4003 | 40.4685 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 2.8422e-14 | 21.9718 | 66.9139 | 112.3006 | 158.1419 | 204.4283 | 251.1482 | 298.2882 | 345.8326 | 393.7638 | 442.0615 | 490.7036 | 539.6651 | 588.9185 | 638.4338 | 688.1779 | 760.6946 | 860.1967 | 956.9284 | 1050.8441 | 1141.254 | 1220.2193 | 1296.3834 | 1369.6889 | 1440.0745 | 1507.4748 | 1547.9433 | 1547.9433 | 1547.9433 | 1547.9433 | 1547.9433
Cash Deficit Loan
| Opening | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Addition | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repayments | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Rate | % | bar: 0 to 26
| Interest Charge | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Minimum Cash Balance | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tariff Workings
| Discount Factor | # |  | 0 | 1 | 0.93044 | 0.86572 | 0.8055 | 0.74947 | 0.69734 | 0.64883 | 0.6037 | 0.5617 | 0.52263 | 0.48628 | 0.45245 | 0.42098 | 0.3917 | 0.36445 | 0.3391 | 0.31551 | 0.29357 | 0.27314 | 0.25415 | 0.23647 | 0.22002 | 0.20471 | 0.19047 | 0.17722 | 0.1649 | 0 | 0 | 0 | 0
| Generation O&M | Rs Cr | 566.6227 | 0 | 5.5726 | 11.7625 | 12.38 | 13.03 | 13.714 | 14.434 | 15.1918 | 15.9894 | 16.8288 | 17.7123 | 18.6422 | 19.621 | 20.6511 | 21.7352 | 22.8763 | 24.0773 | 25.3414 | 26.6718 | 28.0721 | 29.5459 | 31.0971 | 32.7296 | 34.448 | 36.2565 | 38.1599 | 20.0817 | 0 | 0 | 0 | 0
| Infrastructure O&M | Rs Cr | 97.9409 | 0 | 1.1878 | 2.4719 | 2.5651 | 2.6618 | 2.7621 | 2.8663 | 2.9743 | 3.0864 | 3.2028 | 3.3235 | 3.4488 | 3.5789 | 3.7138 | 3.8538 | 3.9991 | 4.1499 | 4.3063 | 4.4687 | 4.6371 | 4.8119 | 4.9933 | 5.1816 | 5.3769 | 5.5797 | 5.79 | 2.9491 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr | 1102.2594 | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| Interest on Term Loan | Rs Cr | 384.8552 | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on WC | Rs Cr | 55.0264 | 0 | 1.1044 | 2.1981 | 2.1885 | 2.1799 | 2.1724 | 2.166 | 2.1607 | 2.1566 | 2.1537 | 2.152 | 2.1516 | 2.1526 | 2.155 | 2.1588 | 2.1641 | 2.171 | 2.1796 | 2.1899 | 2.2019 | 2.2158 | 2.2316 | 2.2494 | 2.2693 | 2.2915 | 2.3159 | 1.2962 | 0 | 0 | 0 | 0
| Interest Income on DSRA | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BG cost for DSRA | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROE | Rs Cr | 1596.3657 | 0 | 31.4127 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 66.9072 | 66.9072 | 66.9072 | 66.9072 | 66.9072 | 33.4536 | 0 | 0 | 0 | 0
| Acc Dep Benefits | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | Rs Cr | 3803.0703 | 0 | 86.884 | 186.1666 | 183.3886 | 180.6475 | 177.9452 | 175.2837 | 172.6651 | 170.0915 | 167.5652 | 165.0886 | 162.6643 | 160.2948 | 157.9831 | 155.7319 | 153.5445 | 119.1174 | 119.6766 | 121.1797 | 122.7604 | 124.4229 | 130.0804 | 131.9191 | 133.8527 | 135.886 | 138.0243 | 70.2062 | 0 | 0 | 0 | 0
| Generation O&M | Rs/kWh | 0.62716 | 0 | 0.32596 | 0.34851 | 0.37145 | 0.3959 | 0.42196 | 0.44973 | 0.47934 | 0.51089 | 0.54451 | 0.58036 | 0.61856 | 0.65927 | 0.70267 | 0.74892 | 0.79821 | 0.85076 | 0.90675 | 0.96644 | 1.0301 | 1.0979 | 1.1701 | 1.2471 | 1.3292 | 1.4167 | 1.51 | 1.3659 | 0 | 0 | 0 | 0
| Infrastructure O&M | Rs/kWh | 0.11342 | 0 | 0.069477 | 0.073239 | 0.076962 | 0.080875 | 0.084986 | 0.089306 | 0.093846 | 0.098617 | 0.10363 | 0.1089 | 0.11443 | 0.12025 | 0.12636 | 0.13279 | 0.13954 | 0.14663 | 0.15409 | 0.16192 | 0.17015 | 0.1788 | 0.18789 | 0.19744 | 0.20748 | 0.21803 | 0.22911 | 0.20059 | 0 | 0 | 0 | 0
| Depreciation | Rs/kWh | 1.6265 | 0 | 1.6925 | 1.7193 | 1.7411 | 1.7631 | 1.7854 | 1.808 | 1.8309 | 1.8541 | 1.8775 | 1.9013 | 1.9254 | 1.9498 | 1.9744 | 1.9994 | 2.0247 | 0.8781 | 0.88922 | 0.90047 | 0.91187 | 0.92341 | 0.9351 | 0.94694 | 0.95892 | 0.97106 | 0.98335 | 0.84517 | 0 | 0 | 0 | 0
| Interest on Term Loan | Rs/kWh | 0.74265 | 0 | 1.0922 | 1.4432 | 1.3571 | 1.2685 | 1.1775 | 1.084 | 0.98798 | 0.88932 | 0.78801 | 0.68398 | 0.5772 | 0.46761 | 0.35514 | 0.23976 | 0.1214 | 0.030734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on WC | Rs/kWh | 0.071544 | 0 | 0.064598 | 0.065128 | 0.065664 | 0.066235 | 0.066842 | 0.067488 | 0.068175 | 0.068906 | 0.069684 | 0.070511 | 0.071391 | 0.072328 | 0.073324 | 0.074384 | 0.075512 | 0.076712 | 0.077989 | 0.079348 | 0.080794 | 0.082333 | 0.08397 | 0.085712 | 0.087566 | 0.089539 | 0.091639 | 0.088166 | 0 | 0 | 0 | 0
| Interest Income on DSRA | Rs/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BG cost for DSRA | Rs/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROE | Rs/kWh | 2.0722 | 0 | 1.8374 | 1.8666 | 1.8902 | 1.9141 | 1.9383 | 1.9629 | 1.9877 | 2.0129 | 2.0384 | 2.0642 | 2.0903 | 2.1168 | 2.1436 | 2.1707 | 2.1982 | 2.226 | 2.2542 | 2.2827 | 2.3116 | 2.3409 | 2.5176 | 2.5494 | 2.5817 | 2.6144 | 2.6475 | 2.2755 | 0 | 0 | 0 | 0
| Acc Dep Benefits | Rs/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | Rs/kWh | 5.2536 | 0 | 5.0821 | 5.5159 | 5.5024 | 5.4887 | 5.4751 | 5.4615 | 5.448 | 5.4347 | 5.4218 | 5.4092 | 5.3973 | 5.386 | 5.3755 | 5.366 | 5.3576 | 4.2089 | 4.2822 | 4.3909 | 4.5045 | 4.6233 | 4.8947 | 5.0267 | 5.1649 | 5.3097 | 5.4616 | 4.7753 | 0 | 0 | 0 | 0
| Levelized Tariff | Rs/kWh | 5.2536 | 0 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 0 | 0 | 0 | 0
Tax Computation
| PBT | Rs Cr |  | 0 | 34.3437 | 54.1432 | 54.7048 | 55.2572 | 55.7982 | 56.3253 | 56.8363 | 57.3286 | 57.7996 | 58.2466 | 58.6668 | 59.0571 | 59.4144 | 59.7356 | 60.0172 | 92.5622 | 90.1444 | 86.8061 | 83.413 | 79.9608 | 76.4451 | 72.8612 | 69.2042 | 65.469 | 61.6502 | 40.4847 | 0 | 0 | 0 | 0
| Book Depreication | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| Tax Depreciation | Rs Cr |  | 0 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Taxable Income |  |  | 0 | -32.275 | 16.6178 | 17.1795 | 17.7319 | 18.2728 | 18.7999 | 19.3109 | 19.8032 | 20.2743 | 20.7213 | 21.1414 | 21.5317 | 21.8891 | 117.7632 | 118.0448 | 117.4135 | 114.9957 | 111.6574 | 108.2642 | 104.8121 | 101.2964 | 97.7125 | 94.0555 | 90.3202 | 86.5014 | 52.9103 | 0 | 0 | 0 | 0
Corporate Tax Calculations
Unabsorbed Depreciation + Business Losses
| Opening | Rs Cr |  | 0 | 0 | 32.275 | 15.6571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Addition | Rs Cr |  | 0 | 32.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Set Off | Rs Cr |  | 0 | 0 | 16.6178 | 15.6571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 0 | 32.275 | 15.6571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Taxable Income after UD + BL | Rs Cr |  | 0 | -32.275 | 0 | 1.5223 | 17.7319 | 18.2728 | 18.7999 | 19.3109 | 19.8032 | 20.2743 | 20.7213 | 21.1414 | 21.5317 | 21.8891 | 117.7632 | 118.0448 | 117.4135 | 114.9957 | 111.6574 | 108.2642 | 104.8121 | 101.2964 | 97.7125 | 94.0555 | 90.3202 | 86.5014 | 52.9103 | 0 | 0 | 0 | 0
| Corporate Tax Rate | % |  | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22% | 22%
| Corporate Tax | Rs Cr |  | 0 | 0 | 0 | 0.33491 | 3.901 | 4.02 | 4.136 | 4.2484 | 4.3567 | 4.4603 | 4.5587 | 4.6511 | 4.737 | 4.8156 | 25.9079 | 25.9699 | 25.831 | 25.299 | 24.5646 | 23.8181 | 23.0587 | 22.2852 | 21.4967 | 20.6922 | 19.8705 | 19.0303 | 11.6403 | 0 | 0 | 0 | 0
MAT Calculations
| Book Profits | Rs Cr |  | 0 | 34.3437 | 54.1432 | 54.7048 | 55.2572 | 55.7982 | 56.3253 | 56.8363 | 57.3286 | 57.7996 | 58.2466 | 58.6668 | 59.0571 | 59.4144 | 59.7356 | 60.0172 | 92.5622 | 90.1444 | 86.8061 | 83.413 | 79.9608 | 76.4451 | 72.8612 | 69.2042 | 65.469 | 61.6502 | 40.4847 | 0 | 0 | 0 | 0
| MAT Rate | % |  | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16%
| MAT | Rs Cr |  | 0 | 5.8934 | 9.291 | 9.3873 | 9.4821 | 9.575 | 9.6654 | 9.7531 | 9.8376 | 9.9184 | 9.9951 | 10.0672 | 10.1342 | 10.1955 | 10.2506 | 10.2989 | 15.8837 | 15.4688 | 14.8959 | 14.3137 | 13.7213 | 13.118 | 12.503 | 11.8754 | 11.2345 | 10.5792 | 6.9472 | 0 | 0 | 0 | 0
MAT Credit
| Opening Balance | Rs Cr |  | 0 | 0 | 5.8934 | 15.1844 | 24.2368 | 29.8179 | 35.3729 | 40.9023 | 46.407 | 51.8879 | 57.346 | 62.7824 | 68.1985 | 73.5958 | 78.9757 | 63.3184 | 47.6475 | 37.7002 | 27.8699 | 18.2012 | 8.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Additions | Rs Cr |  | 0 | 5.8934 | 9.291 | 9.0524 | 5.5811 | 5.555 | 5.5294 | 5.5047 | 5.4809 | 5.4581 | 5.4364 | 5.4161 | 5.3972 | 5.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Used | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6573 | 15.6709 | 9.9473 | 9.8303 | 9.6687 | 9.5045 | 8.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expired | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing Balance | Rs Cr |  | 0 | 5.8934 | 15.1844 | 24.2368 | 29.8179 | 35.3729 | 40.9023 | 46.407 | 51.8879 | 57.346 | 62.7824 | 68.1985 | 73.5958 | 78.9757 | 63.3184 | 47.6475 | 37.7002 | 27.8699 | 18.2012 | 8.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tax Payable
| MAT payable | Rs Cr |  | 0 | 5.8934 | 9.291 | 9.3873 | 9.4821 | 9.575 | 9.6654 | 9.7531 | 9.8376 | 9.9184 | 9.9951 | 10.0672 | 10.1342 | 10.1955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Corporate Tax Payable | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9079 | 25.9699 | 25.831 | 25.299 | 24.5646 | 23.8181 | 23.0587 | 22.2852 | 21.4967 | 20.6922 | 19.8705 | 19.0303 | 11.6403 | 0 | 0 | 0 | 0
| MAT Credit offset | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6573 | 15.6709 | 9.9473 | 9.8303 | 9.6687 | 9.5045 | 8.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Effective Tax Payable | Rs Cr |  | 0 | 5.8934 | 9.291 | 9.3873 | 9.4821 | 9.575 | 9.6654 | 9.7531 | 9.8376 | 9.9184 | 9.9951 | 10.0672 | 10.1342 | 10.1955 | 10.2506 | 10.2989 | 15.8837 | 15.4688 | 14.8959 | 14.3137 | 14.3619 | 22.2852 | 21.4967 | 20.6922 | 19.8705 | 19.0303 | 11.6403 | 0 | 0 | 0 | 0
| Effective Tax rate | % |  | 0% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.16% | 17.96% | 29.15% | 29.5% | 29.9% | 30.35% | 30.87% | 28.75% | 0% | 0% | 0% | 0%
Financial Statements & IRR
P&L Account
| Revenue | Rs Cr |  | 0 | 89.815 | 177.3117 | 175.0953 | 172.9066 | 170.7453 | 168.611 | 166.5034 | 164.4221 | 162.3668 | 160.3372 | 158.333 | 156.3538 | 154.3994 | 152.4694 | 150.5635 | 148.6815 | 146.823 | 144.9877 | 143.1753 | 141.3857 | 139.6183 | 137.8731 | 136.1497 | 134.4478 | 132.7672 | 77.2372 | 0 | 0 | 0 | 0
Expenditure
| Generation O&M | Rs Cr |  | 0 | 5.5726 | 11.7625 | 12.38 | 13.03 | 13.714 | 14.434 | 15.1918 | 15.9894 | 16.8288 | 17.7123 | 18.6422 | 19.621 | 20.6511 | 21.7352 | 22.8763 | 24.0773 | 25.3414 | 26.6718 | 28.0721 | 29.5459 | 31.0971 | 32.7296 | 34.448 | 36.2565 | 38.1599 | 20.0817 | 0 | 0 | 0 | 0
| Infrastructure O&M | Rs Cr |  | 0 | 1.1878 | 2.4719 | 2.5651 | 2.6618 | 2.7621 | 2.8663 | 2.9743 | 3.0864 | 3.2028 | 3.3235 | 3.4488 | 3.5789 | 3.7138 | 3.8538 | 3.9991 | 4.1499 | 4.3063 | 4.4687 | 4.6371 | 4.8119 | 4.9933 | 5.1816 | 5.3769 | 5.5797 | 5.79 | 2.9491 | 0 | 0 | 0 | 0
| PBITDA | Rs Cr |  | 0 | 83.0547 | 163.0774 | 160.1502 | 157.2149 | 154.2691 | 151.3107 | 148.3372 | 145.3462 | 142.3352 | 139.3013 | 136.2419 | 133.154 | 130.0346 | 126.8804 | 123.6881 | 120.4543 | 117.1753 | 113.8472 | 110.4661 | 107.0278 | 103.5279 | 99.9619 | 96.3248 | 92.6117 | 88.8173 | 54.2065 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| PBIT | Rs Cr |  | 0 | 54.1203 | 105.0497 | 102.1226 | 99.1873 | 96.2415 | 93.2831 | 90.3096 | 87.3186 | 84.3075 | 81.2737 | 78.2143 | 75.1264 | 72.0069 | 68.8527 | 65.6605 | 95.6031 | 92.324 | 88.996 | 85.6149 | 82.1766 | 78.6767 | 75.1106 | 71.4736 | 67.7605 | 63.966 | 41.7809 | 0 | 0 | 0 | 0
| Interest on Loan | Rs Cr |  | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on WC Loan | Rs Cr |  | 0 | 1.1044 | 2.1981 | 2.1885 | 2.1799 | 2.1724 | 2.166 | 2.1607 | 2.1566 | 2.1537 | 2.152 | 2.1516 | 2.1526 | 2.155 | 2.1588 | 2.1641 | 2.171 | 2.1796 | 2.1899 | 2.2019 | 2.2158 | 2.2316 | 2.2494 | 2.2693 | 2.2915 | 2.3159 | 1.2962 | 0 | 0 | 0 | 0
| Interest on Cash Deficit Loan | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Income on DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BG Cost on DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Profits Before Tax (PBT) | Rs Cr |  | 0 | 34.3437 | 54.1432 | 54.7048 | 55.2572 | 55.7982 | 56.3253 | 56.8363 | 57.3286 | 57.7996 | 58.2466 | 58.6668 | 59.0571 | 59.4144 | 59.7356 | 60.0172 | 92.5622 | 90.1444 | 86.8061 | 83.413 | 79.9608 | 76.4451 | 72.8612 | 69.2042 | 65.469 | 61.6502 | 40.4847 | 0 | 0 | 0 | 0
| Tax | Rs Cr |  | 0 | 5.8934 | 9.291 | 9.3873 | 9.4821 | 9.575 | 9.6654 | 9.7531 | 9.8376 | 9.9184 | 9.9951 | 10.0672 | 10.1342 | 10.1955 | 10.2506 | 10.2989 | 15.8837 | 15.4688 | 14.8959 | 14.3137 | 14.3619 | 22.2852 | 21.4967 | 20.6922 | 19.8705 | 19.0303 | 11.6403 | 0 | 0 | 0 | 0
| Profits After Tax (PAT) | Rs Cr |  | 0 | 28.4504 | 44.8522 | 45.3175 | 45.7751 | 46.2232 | 46.6599 | 47.0832 | 47.491 | 47.8812 | 48.2515 | 48.5996 | 48.9229 | 49.2189 | 49.485 | 49.7182 | 76.6785 | 74.6756 | 71.9102 | 69.0993 | 65.5989 | 54.1599 | 51.3645 | 48.512 | 45.5985 | 42.6198 | 28.8444 | 0 | 0 | 0 | 0
Cash flow statement
| Revenue | Rs Cr |  | 0 | 89.815 | 177.3117 | 175.0953 | 172.9066 | 170.7453 | 168.611 | 166.5034 | 164.4221 | 162.3668 | 160.3372 | 158.333 | 156.3538 | 154.3994 | 152.4694 | 150.5635 | 148.6815 | 146.823 | 144.9877 | 143.1753 | 141.3857 | 139.6183 | 137.8731 | 136.1497 | 134.4478 | 132.7672 | 77.2372 | 0 | 0 | 0 | 0
| Generation O&M | Rs Cr |  | 0 | -5.5726 | -11.7625 | -12.38 | -13.03 | -13.714 | -14.434 | -15.1918 | -15.9894 | -16.8288 | -17.7123 | -18.6422 | -19.621 | -20.6511 | -21.7352 | -22.8763 | -24.0773 | -25.3414 | -26.6718 | -28.0721 | -29.5459 | -31.0971 | -32.7296 | -34.448 | -36.2565 | -38.1599 | -20.0817 | 0 | 0 | 0 | 0
| Infrastructure O&M | Rs Cr |  | 0 | -1.1878 | -2.4719 | -2.5651 | -2.6618 | -2.7621 | -2.8663 | -2.9743 | -3.0864 | -3.2028 | -3.3235 | -3.4488 | -3.5789 | -3.7138 | -3.8538 | -3.9991 | -4.1499 | -4.3063 | -4.4687 | -4.6371 | -4.8119 | -4.9933 | -5.1816 | -5.3769 | -5.5797 | -5.79 | -2.9491 | 0 | 0 | 0 | 0
| Taxes | Rs Cr |  | 0 | -5.8934 | -9.291 | -9.3873 | -9.4821 | -9.575 | -9.6654 | -9.7531 | -9.8376 | -9.9184 | -9.9951 | -10.0672 | -10.1342 | -10.1955 | -10.2506 | -10.2989 | -15.8837 | -15.4688 | -14.8959 | -14.3137 | -14.3619 | -22.2852 | -21.4967 | -20.6922 | -19.8705 | -19.0303 | -11.6403 | 0 | 0 | 0 | 0
| Change in DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Income on DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BG Cost on DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Change in WC | Rs Cr |  | 0 | -25.6789 | 0.19361 | 0.11121 | 0.099367 | 0.087135 | 0.074495 | 0.061424 | 0.047898 | 0.033889 | 0.019371 | 0.0043145 | -0.011311 | -0.027536 | -0.044395 | -0.061924 | -0.080158 | -0.099138 | -0.1189 | -0.1395 | -0.16096 | -0.18335 | -0.20671 | -0.23109 | -0.25655 | -0.28315 | -3.2061 | 0 | 0 | 0 | 0
| Cash Flow from Operating Activities | Rs Cr |  | 0 | 51.4823 | 153.98 | 150.8741 | 147.8321 | 144.7813 | 141.7198 | 138.6455 | 135.5565 | 132.4506 | 129.3256 | 126.179 | 123.0085 | 119.8115 | 116.5853 | 113.3272 | 104.4905 | 101.6073 | 98.8324 | 96.013 | 92.505 | 81.0594 | 78.2584 | 75.4015 | 72.4847 | 69.5038 | 39.3601 | 0 | 0 | 0 | 0
| Capital Expenditure | Rs Cr |  | -582.0486 | -660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cash Flow from Investing Activities | Rs Cr |  | -582.0486 | -660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commerical Loan 1 - Additions | Rs Cr |  | 407.434 | 462.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commercial Loan - Additions | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grant | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equity | Rs Cr |  | 174.6146 | 198.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cash Deficit Loan | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commerical Loan 1 - Repayment | Rs Cr |  | 0 | -28.9931 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commercial Loan 2 - Repayment | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cash Deficit Loan Repayment | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Change in WC Loan | Rs Cr |  | 0 | 19.2592 | -0.14521 | -0.083411 | -0.074525 | -0.065351 | -0.055871 | -0.046068 | -0.035923 | -0.025417 | -0.014528 | -0.0032359 | 0.0084829 | 0.020652 | 0.033297 | 0.046443 | 0.060119 | 0.074353 | 0.089177 | 0.10462 | 0.12072 | 0.13751 | 0.15503 | 0.17332 | 0.19241 | 0.21236 | 2.4046 | 0 | 0 | 0 | 0
| Interest on Debt | Rs Cr |  | 0 | -18.6722 | -48.7084 | -45.2293 | -41.7501 | -38.2709 | -34.7917 | -31.3126 | -27.8334 | -24.3542 | -20.875 | -17.3959 | -13.9167 | -10.4375 | -6.9583 | -3.4792 | -0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on WC Loan | Rs Cr |  | 0 | -1.1044 | -2.1981 | -2.1885 | -2.1799 | -2.1724 | -2.166 | -2.1607 | -2.1566 | -2.1537 | -2.152 | -2.1516 | -2.1526 | -2.155 | -2.1588 | -2.1641 | -2.171 | -2.1796 | -2.1899 | -2.2019 | -2.2158 | -2.2316 | -2.2494 | -2.2693 | -2.2915 | -2.3159 | -1.2962 | 0 | 0 | 0 | 0
| Interest on Cash Deficit Loan | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cash Flow from Financing Activities | Rs Cr |  | 582.0486 | 631.003 | -109.038 | -105.4874 | -101.9908 | -98.4949 | -94.9998 | -91.5056 | -88.0121 | -84.5195 | -81.0278 | -77.5369 | -74.047 | -70.5581 | -67.0701 | -63.5831 | -31.9738 | -2.1052 | -2.1007 | -2.0973 | -2.095 | -2.0941 | -2.0944 | -2.096 | -2.0991 | -2.1035 | 1.1084 | 0 | 0 | 0 | 0
Cash Schedule
| Opening cash balance | Rs Cr |  | 0 | 0 | 21.9718 | 66.9139 | 112.3006 | 158.1419 | 204.4283 | 251.1482 | 298.2882 | 345.8326 | 393.7638 | 442.0615 | 490.7036 | 539.6651 | 588.9185 | 638.4338 | 688.1779 | 760.6946 | 860.1967 | 956.9284 | 1050.8441 | 1141.254 | 1220.2193 | 1296.3834 | 1369.6889 | 1440.0745 | 1507.4748 | 1547.9433 | 1547.9433 | 1547.9433 | 1547.9433
| Cash generated during the year | Rs Cr |  | 0 | 21.9718 | 44.942 | 45.3867 | 45.8413 | 46.2864 | 46.7199 | 47.14 | 47.5444 | 47.9311 | 48.2978 | 48.6421 | 48.9615 | 49.2534 | 49.5153 | 49.7442 | 72.5166 | 99.5021 | 96.7317 | 93.9157 | 90.4099 | 78.9653 | 76.164 | 73.3055 | 70.3856 | 67.4003 | 40.4685 | 0 | 0 | 0 | 0
| Closing Cash Balance | Rs Cr |  | 0 | 21.9718 | 66.9139 | 112.3006 | 158.1419 | 204.4283 | 251.1482 | 298.2882 | 345.8326 | 393.7638 | 442.0615 | 490.7036 | 539.6651 | 588.9185 | 638.4338 | 688.1779 | 760.6946 | 860.1967 | 956.9284 | 1050.8441 | 1141.254 | 1220.2193 | 1296.3834 | 1369.6889 | 1440.0745 | 1507.4748 | 1547.9433 | 1547.9433 | 1547.9433 | 1547.9433 | 1547.9433
Balance Sheet Statement
Assets
| GFA | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Accumulated Depreciation | Rs Cr |  | 0 | 28.9343 | 86.962 | 144.9896 | 203.0173 | 261.0449 | 319.0726 | 377.1002 | 435.1279 | 493.1555 | 551.1832 | 609.2108 | 667.2384 | 725.2661 | 783.2937 | 841.3214 | 866.1726 | 891.0239 | 915.8751 | 940.7264 | 965.5776 | 990.4288 | 1015.2801 | 1040.1313 | 1064.9826 | 1089.8338 | 1102.2594 | 1102.2594 | 1102.2594 | 1102.2594 | 1102.2594
| Net Fixed Assets | Rs Cr |  | 0 | 1213.6277 | 1155.6001 | 1097.5724 | 1039.5448 | 981.5171 | 923.4895 | 865.4618 | 807.4342 | 749.4065 | 691.3789 | 633.3512 | 575.3236 | 517.2959 | 459.2683 | 401.2406 | 376.3894 | 351.5382 | 326.6869 | 301.8357 | 276.9844 | 252.1332 | 227.282 | 202.4307 | 177.5795 | 152.7282 | 140.3026 | 140.3026 | 140.3026 | 140.3026 | 140.3026
| CWIP | Rs Cr |  | 582.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Current Assets | Rs Cr |  | 0 | 25.6789 | 25.4853 | 25.3741 | 25.2747 | 25.1876 | 25.1131 | 25.0517 | 25.0038 | 24.9699 | 24.9505 | 24.9462 | 24.9575 | 24.9851 | 25.0295 | 25.0914 | 25.1715 | 25.2707 | 25.3896 | 25.5291 | 25.69 | 25.8734 | 26.0801 | 26.3112 | 26.5677 | 26.8509 | 30.057 | 30.057 | 30.057 | 30.057 | 30.057
| DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cash & Bank Balance | Rs Cr |  | 0 | 21.9718 | 66.9139 | 112.3006 | 158.1419 | 204.4283 | 251.1482 | 298.2882 | 345.8326 | 393.7638 | 442.0615 | 490.7036 | 539.6651 | 588.9185 | 638.4338 | 688.1779 | 760.6946 | 860.1967 | 956.9284 | 1050.8441 | 1141.254 | 1220.2193 | 1296.3834 | 1369.6889 | 1440.0745 | 1507.4748 | 1547.9433 | 1547.9433 | 1547.9433 | 1547.9433 | 1547.9433
| TOTAL ASSETS | Rs Cr |  | 582.0486 | 1261.2785 | 1247.9992 | 1235.2471 | 1222.9614 | 1211.133 | 1199.7508 | 1188.8017 | 1178.2706 | 1168.1402 | 1158.3909 | 1149.001 | 1139.9462 | 1131.1995 | 1122.7315 | 1114.51 | 1162.2555 | 1237.0055 | 1309.0049 | 1378.2088 | 1443.9285 | 1498.2259 | 1549.7454 | 1598.4308 | 1644.2217 | 1687.0539 | 1718.3029 | 1718.3029 | 1718.3029 | 1718.3029 | 1718.3029
Liabilities
| Equity | Rs Cr |  | 174.6146 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686
| Reserve and Surplus | Rs Cr |  | 0 | 28.4504 | 73.3026 | 118.62 | 164.3951 | 210.6183 | 257.2782 | 304.3614 | 351.8524 | 399.7337 | 447.9852 | 496.5847 | 545.5076 | 594.7265 | 644.2115 | 693.9297 | 770.6082 | 845.2839 | 917.1941 | 986.2934 | 1051.8924 | 1106.0523 | 1157.4167 | 1205.9288 | 1251.5273 | 1294.1471 | 1322.9915 | 1322.9915 | 1322.9915 | 1322.9915 | 1322.9915
| Grants | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commercial Loan 1 | Rs Cr |  | 407.434 | 840.8003 | 782.8141 | 724.8279 | 666.8416 | 608.8554 | 550.8692 | 492.8829 | 434.8967 | 376.9105 | 318.9243 | 260.938 | 202.9518 | 144.9656 | 86.9793 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commercial Loan 2 | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Working Capital Loan | Rs Cr |  | 0 | 19.2592 | 19.114 | 19.0306 | 18.9561 | 18.8907 | 18.8348 | 18.7888 | 18.7528 | 18.7274 | 18.7129 | 18.7097 | 18.7181 | 18.7388 | 18.7721 | 18.8185 | 18.8787 | 18.953 | 19.0422 | 19.1468 | 19.2675 | 19.405 | 19.5601 | 19.7334 | 19.9258 | 20.1382 | 22.5427 | 22.5427 | 22.5427 | 22.5427 | 22.5427
| Cash Deficit Loan | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL LIABILITIES | Rs Cr |  | 582.0486 | 1261.2785 | 1247.9992 | 1235.2471 | 1222.9614 | 1211.133 | 1199.7508 | 1188.8017 | 1178.2706 | 1168.1402 | 1158.3909 | 1149.001 | 1139.9462 | 1131.1995 | 1122.7315 | 1114.51 | 1162.2555 | 1237.0055 | 1309.0049 | 1378.2088 | 1443.9285 | 1498.2259 | 1549.7454 | 1598.4308 | 1644.2217 | 1687.0539 | 1718.3029 | 1718.3029 | 1718.3029 | 1718.3029 | 1718.3029
| Check | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSCR
| PAT | Rs Cr |  | 0 | 28.4504 | 44.8522 | 45.3175 | 45.7751 | 46.2232 | 46.6599 | 47.0832 | 47.491 | 47.8812 | 48.2515 | 48.5996 | 48.9229 | 49.2189 | 49.485 | 49.7182 | 76.6785 | 74.6756 | 71.9102 | 69.0993 | 65.5989 | 54.1599 | 51.3645 | 48.512 | 45.5985 | 42.6198 | 28.8444 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| Interest on Debt | Rs Cr |  | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | Rs Cr |  | 0 | 76.0569 | 151.5883 | 148.5744 | 145.5528 | 142.5218 | 139.4793 | 136.4234 | 133.3521 | 130.2631 | 127.1542 | 124.0231 | 120.8672 | 117.6841 | 114.471 | 111.225 | 102.3996 | 99.5269 | 96.7614 | 93.9506 | 90.4502 | 79.0112 | 76.2157 | 73.3633 | 70.4498 | 67.4711 | 41.27 | 0 | 0 | 0 | 0
| Interest on Debt | Rs Cr |  | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Debt Repayment | Rs Cr |  | 0 | 28.9931 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | Rs Cr |  | 0 | 48 | 107 | 103 | 100 | 96 | 93 | 89 | 86 | 82 | 79 | 75 | 72 | 68 | 65 | 61 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DSCR | # |  | 0 | 1.5845 | 1.4167 | 1.4425 | 1.4555 | 1.4846 | 1.4998 | 1.5328 | 1.5506 | 1.5886 | 1.6095 | 1.6536 | 1.6787 | 1.7306 | 1.7611 | 1.8234 | 3.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Average DSCR | # | 2.2409
| Minimum DSCR | # | 0
Project IRR
| PAT | Rs Cr |  | 0 | 28.4504 | 44.8522 | 45.3175 | 45.7751 | 46.2232 | 46.6599 | 47.0832 | 47.491 | 47.8812 | 48.2515 | 48.5996 | 48.9229 | 49.2189 | 49.485 | 49.7182 | 76.6785 | 74.6756 | 71.9102 | 69.0993 | 65.5989 | 54.1599 | 51.3645 | 48.512 | 45.5985 | 42.6198 | 28.8444 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| Tax Shield | Rs Cr |  | 0 | -3.3937 | -8.7356 | -8.1369 | -7.5384 | -6.9401 | -6.3419 | -5.744 | -5.1463 | -4.5488 | -3.9514 | -3.3543 | -2.7575 | -2.1609 | -1.5645 | -0.96839 | -0.52181 | -0.37402 | -0.37578 | -0.37784 | -0.39798 | -0.65055 | -0.66366 | -0.67854 | -0.69548 | -0.71487 | -0.37269 | 0 | 0 | 0 | 0
| Interest on Debt | Rs Cr |  | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on WC Loan | Rs Cr |  | 0 | 1.1044 | 2.1981 | 2.1885 | 2.1799 | 2.1724 | 2.166 | 2.1607 | 2.1566 | 2.1537 | 2.152 | 2.1516 | 2.1526 | 2.155 | 2.1588 | 2.1641 | 2.171 | 2.1796 | 2.1899 | 2.2019 | 2.2158 | 2.2316 | 2.2494 | 2.2693 | 2.2915 | 2.3159 | 1.2962 | 0 | 0 | 0 | 0
| Interest on Cash Deficit Loan | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Change in WC | Rs Cr |  | 0 | -25.6789 | 0.19361 | 0.11121 | 0.099367 | 0.087135 | 0.074495 | 0.061424 | 0.047898 | 0.033889 | 0.019371 | 0.0043145 | -0.011311 | -0.027536 | -0.044395 | -0.061924 | -0.080158 | -0.099138 | -0.1189 | -0.1395 | -0.16096 | -0.18335 | -0.20671 | -0.23109 | -0.25655 | -0.28315 | -3.2061 | 0 | 0 | 0 | 0
| CapEX | Rs Cr |  | -582.0486 | -660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Terminal Value | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.3596 | 0 | 0 | 0 | 0
| Dismantling Cost | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1064 | 0 | 0 | 0 | 0
| FCFF | Rs Cr |  | -582.0486 | -612.4248 | 145.2444 | 142.7372 | 140.2937 | 137.8412 | 135.3778 | 132.9015 | 130.4103 | 127.9019 | 125.3741 | 122.8247 | 120.251 | 117.6506 | 115.0208 | 112.3589 | 103.9687 | 101.2333 | 98.4566 | 95.6351 | 92.107 | 80.4088 | 77.5948 | 74.723 | 71.7892 | 68.789 | 206.2406 | 0 | 0 | 0 | 0
|  |  |  | 0 | -612.4248 | 135.1413 | 123.5703 | 113.0066 | 103.3078 | 94.4039 | 86.2305 | 78.7284 | 71.8431 | 65.5246 | 59.727 | 54.4079 | 49.5286 | 45.0534 | 40.9493 | 35.2558 | 31.9403 | 28.9034 | 26.1222 | 23.4085 | 19.014 | 17.0723 | 15.2968 | 13.674 | 12.1911 | 34.0085 | 0 | 0 | 0 | 0
| Project IRR | # | 8.796%
| NPV @ WACC | Rs Cr | 12.1938
Equity IRR
| PAT | Rs Cr |  | 0 | 28.4504 | 44.8522 | 45.3175 | 45.7751 | 46.2232 | 46.6599 | 47.0832 | 47.491 | 47.8812 | 48.2515 | 48.5996 | 48.9229 | 49.2189 | 49.485 | 49.7182 | 76.6785 | 74.6756 | 71.9102 | 69.0993 | 65.5989 | 54.1599 | 51.3645 | 48.512 | 45.5985 | 42.6198 | 28.8444 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256 | 0 | 0 | 0 | 0
| Repayment | Rs Cr |  | 0 | -28.9931 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Change in WC | Rs Cr |  | 0 | -25.6789 | 0.19361 | 0.11121 | 0.099367 | 0.087135 | 0.074495 | 0.061424 | 0.047898 | 0.033889 | 0.019371 | 0.0043145 | -0.011311 | -0.027536 | -0.044395 | -0.061924 | -0.080158 | -0.099138 | -0.1189 | -0.1395 | -0.16096 | -0.18335 | -0.20671 | -0.23109 | -0.25655 | -0.28315 | -3.2061 | 0 | 0 | 0 | 0
| CapEX | Rs Cr |  | -582.0486 | -660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Increase in Debt | Rs Cr |  | 407.434 | 462.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Change in DSRA | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Increase/ (Decrease) in Cash Deficit Loan | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Increase/ (Decrease) in WC Loan | Rs Cr |  | 0 | 19.2592 | -0.14521 | -0.083411 | -0.074525 | -0.065351 | -0.055871 | -0.046068 | -0.035923 | -0.025417 | -0.014528 | -0.0032359 | 0.0084829 | 0.020652 | 0.033297 | 0.046443 | 0.060119 | 0.074353 | 0.089177 | 0.10462 | 0.12072 | 0.13751 | 0.15503 | 0.17332 | 0.19241 | 0.21236 | 2.4046 | 0 | 0 | 0 | 0
| Terminal Value | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.8169 | 0 | 0 | 0 | 0
| Dismantling Cost | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1064 | 0 | 0 | 0 | 0
| FCFE | Rs Cr |  | -174.6146 | -176.1822 | 44.942 | 45.3867 | 45.8413 | 46.2864 | 46.7199 | 47.14 | 47.5444 | 47.9311 | 48.2978 | 48.6421 | 48.9615 | 49.2534 | 49.5153 | 49.7442 | 72.5166 | 99.5021 | 96.7317 | 93.9157 | 90.4099 | 78.9653 | 76.164 | 73.3055 | 70.3856 | 67.4003 | 185.1789 | 0 | 0 | 0 | 0
| Equity IRR | # | 13.42%
| NPV @ 10% | Rs Cr | 108.0408
Economic IRR
Avoided Fuel Cost
| Enery Charge | Rs/ kWh | 4
| Escalation in Total Charge | % | 2%
| Net Energy Charge | Rs/ kWh |  | 0 | 4.0397 | 4.1205 | 4.2029 | 4.287 | 4.3727 | 4.4601 | 4.5493 | 4.6403 | 4.7331 | 4.8278 | 4.9244 | 5.0228 | 5.1233 | 5.2258 | 5.3303 | 5.4369 | 5.5456 | 5.6565 | 5.7697 | 5.8851 | 6.0028 | 6.1228 | 6.2453 | 6.3702 | 6.4976 | 6.5622 | 0 | 0 | 0 | 0
| Levelized Tariff-Solar | Rs/ kWh | 5.2536 | 0 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 5.2536 | 0 | 0 | 0 | 0
| Net Generation-Solar | MU |  | 0 | 170.9605 | 337.5083 | 333.2894 | 329.1233 | 325.0093 | 320.9467 | 316.9348 | 312.9732 | 309.061 | 305.1977 | 301.3828 | 297.6155 | 293.8953 | 290.2216 | 286.5938 | 283.0114 | 279.4738 | 275.9803 | 272.5306 | 269.1239 | 265.7599 | 262.4379 | 259.1574 | 255.918 | 252.719 | 147.019 | 0 | 0 | 0 | 0
| Avoided Fuel Cost | Rs / kWh |  | 0 | -1.2139 | -1.1331 | -1.0507 | -0.9666 | -0.88086 | -0.7934 | -0.7042 | -0.61321 | -0.52041 | -0.42575 | -0.32919 | -0.2307 | -0.13025 | -0.027779 | 0.076737 | 0.18334 | 0.29208 | 0.40299 | 0.51612 | 0.63152 | 0.74922 | 0.86927 | 0.99173 | 1.1166 | 1.244 | 1.3087 | 0 | 0 | 0 | 0
| Resource cost saving | Rs Cr | -66.5102 | 0 | -20.7522 | -38.2419 | -35.0172 | -31.813 | -28.6287 | -25.4641 | -22.3186 | -19.192 | -16.0838 | -12.9937 | -9.9212 | -6.866 | -3.8278 | -0.8062 | 2.1992 | 5.1888 | 8.1629 | 11.1218 | 14.066 | 16.9956 | 19.9112 | 22.813 | 25.7014 | 28.5767 | 31.4393 | 19.2403 | 0 | 0 | 0 | 0
| Savings |  | -136.7468 | 0 | -20.7522 | -35.5818 | -30.3151 | -25.6254 | -21.4564 | -17.757 | -14.481 | -11.5862 | -9.0343 | -6.7909 | -4.8245 | -3.1066 | -1.6114 | -0.31579 | 0.80151 | 1.7595 | 2.5755 | 3.265 | 3.842 | 4.3194 | 4.7083 | 5.0193 | 5.2614 | 5.4431 | 5.5718 | 3.1727 | 0 | 0 | 0 | 0
| Cost of using Fossil Fuel |  |  | 0 | 69.0628 | 139.0698 | 140.0781 | 141.0937 | 142.1166 | 143.1469 | 144.1847 | 145.2301 | 146.283 | 147.3436 | 148.4118 | 149.4878 | 150.5716 | 151.6632 | 152.7628 | 153.8703 | 154.9859 | 156.1095 | 157.2413 | 158.3813 | 159.5296 | 160.6862 | 161.8511 | 163.0245 | 164.2065 | 96.4775 | 0 | 0 | 0 | 0
| Cost of using Non-Fossil fuel |  |  | 0 | 89.815 | 177.3117 | 175.0953 | 172.9066 | 170.7453 | 168.611 | 166.5034 | 164.4221 | 162.3668 | 160.3372 | 158.333 | 156.3538 | 154.3994 | 152.4694 | 150.5635 | 148.6815 | 146.823 | 144.9877 | 143.1753 | 141.3857 | 139.6183 | 137.8731 | 136.1497 | 134.4478 | 132.7672 | 77.2372 | 0 | 0 | 0 | 0
| CO2 Emission Avoided |  |  | 1: -20.7522
| Net Generation | MU | 0 | 0 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 26494 | 0 | 0 | 0 | 0
| Net Generation-Solar | MU |  | 0 | 170.9605 | 337.5083 | 333.2894 | 329.1233 | 325.0093 | 320.9467 | 316.9348 | 312.9732 | 309.061 | 305.1977 | 301.3828 | 297.6155 | 293.8953 | 290.2216 | 286.5938 | 283.0114 | 279.4738 | 275.9803 | 272.5306 | 269.1239 | 265.7599 | 262.4379 | 259.1574 | 255.918 | 252.719 | 147.019 | 0 | 0 | 0 | 0
| CO2 Emissions | million tonne |  | 0 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 29.8686 | 0 | 0 | 0 | 0
| CO2 emission savings | t-CO2 |  | 0 | 192736.1315 | 380497.425 | 375741.2072 | 371044.4421 | 366406.3866 | 361826.3067 | 357303.4779 | 352837.1844 | 348426.7196 | 344071.3856 | 339770.4933 | 335523.3621 | 331329.3201 | 327187.7036 | 323097.8573 | 319059.1341 | 315070.8949 | 311132.5087 | 307243.3524 | 303402.8105 | 299610.2753 | 295865.1469 | 292166.8326 | 288514.7472 | 284908.3128 | 165745.1611 | 0 | 0 | 0 | 0
| Economic Cost of CO2 Emission Savings | Rs/ ton | 7138 | 0 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 7138 | 0 | 0 | 0 | 0
| CO2 emission savings | Rs Cr |  | 0 | 137.5751 | 271.5991 | 268.2041 | 264.8515 | 261.5409 | 258.2716 | 255.0432 | 251.8552 | 248.707 | 245.5982 | 242.5282 | 239.4966 | 236.5029 | 233.5466 | 230.6273 | 227.7444 | 224.8976 | 222.0864 | 219.3103 | 216.5689 | 213.8618 | 211.1885 | 208.5487 | 205.9418 | 203.3676 | 118.3089 | 0 | 0 | 0 | 0
Manpower Growth
| No of Manpower | No. | 60 | 0 | 59.4059 | 60 | 60.6 | 61.206 | 61.8181 | 62.4362 | 63.0606 | 63.6912 | 64.3281 | 64.9714 | 65.6211 | 66.2773 | 66.9401 | 67.6095 | 68.2856 | 68.9685 | 69.6581 | 70.3547 | 71.0583 | 71.7688 | 72.4865 | 73.2114 | 73.9435 | 74.683 | 75.4298 | 76.1841 | 0 | 0 | 0 | 0
| Escalation in Manpower | % | 1%
| Remuneration per person | Rs Cr | 0.02833 | 0 | 0.027504 | 0.02833 | 0.029179 | 0.030055 | 0.030957 | 0.031885 | 0.032842 | 0.033827 | 0.034842 | 0.035887 | 0.036964 | 0.038073 | 0.039215 | 0.040391 | 0.041603 | 0.042851 | 0.044137 | 0.045461 | 0.046825 | 0.048229 | 0.049676 | 0.051166 | 0.052701 | 0.054282 | 0.055911 | 0.057588 | 0 | 0 | 0 | 0
| Escalation in Remuneration | % | 3%
| Job Creation | Rs Cr |  | 0 | 1.6339 | 1.6998 | 1.7683 | 1.8395 | 1.9137 | 1.9908 | 2.071 | 2.1545 | 2.2413 | 2.3316 | 2.4256 | 2.5234 | 2.625 | 2.7308 | 2.8409 | 2.9554 | 3.0745 | 3.1984 | 3.3273 | 3.4614 | 3.6009 | 3.746 | 3.8969 | 4.054 | 4.2173 | 4.3873 | 0 | 0 | 0 | 0
Economic Benefit
| Avoided Fuel Cost | Rs Cr | -66.5102 | 0 | -20.7522 | -38.2419 | -35.0172 | -31.813 | -28.6287 | -25.4641 | -22.3186 | -19.192 | -16.0838 | -12.9937 | -9.9212 | -6.866 | -3.8278 | -0.8062 | 2.1992 | 5.1888 | 8.1629 | 11.1218 | 14.066 | 16.9956 | 19.9112 | 22.813 | 25.7014 | 28.5767 | 31.4393 | 19.2403 | 0 | 0 | 0 | 0
| Reduced Carbon Emissions | Rs Cr | 5917.7722 | 0 | 137.5751 | 271.5991 | 268.2041 | 264.8515 | 261.5409 | 258.2716 | 255.0432 | 251.8552 | 248.707 | 245.5982 | 242.5282 | 239.4966 | 236.5029 | 233.5466 | 230.6273 | 227.7444 | 224.8976 | 222.0864 | 219.3103 | 216.5689 | 213.8618 | 211.1885 | 208.5487 | 205.9418 | 203.3676 | 118.3089 | 0 | 0 | 0 | 0
| Incremental Benefits | Rs Cr | 72.7094 | 0 | 1.6339 | 1.6998 | 1.7683 | 1.8395 | 1.9137 | 1.9908 | 2.071 | 2.1545 | 2.2413 | 2.3316 | 2.4256 | 2.5234 | 2.625 | 2.7308 | 2.8409 | 2.9554 | 3.0745 | 3.1984 | 3.3273 | 3.4614 | 3.6009 | 3.746 | 3.8969 | 4.054 | 4.2173 | 4.3873 | 0 | 0 | 0 | 0
| Total Benefits | Rs Cr | 5923.9713 | 0 | 118.4568 | 235.0569 | 234.9551 | 234.8781 | 234.8258 | 234.7983 | 234.7956 | 234.8177 | 234.8645 | 234.9361 | 235.0326 | 235.1539 | 235.3001 | 235.4712 | 235.6674 | 235.8886 | 236.135 | 236.4066 | 236.7035 | 237.0259 | 237.3739 | 237.7476 | 238.147 | 238.5725 | 239.0242 | 141.9365 | 0 | 0 | 0 | 0
| Capital Expenditure | Rs Cr | -1109.1873 | -519.5723 | -589.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&M Cost | Rs Cr | -664.5635 | 0 | -6.7603 | -14.2344 | -14.9451 | -15.6917 | -16.4762 | -17.3003 | -18.1661 | -19.0758 | -20.0316 | -21.0359 | -22.0911 | -23.1998 | -24.3649 | -25.589 | -26.8754 | -28.2272 | -29.6477 | -31.1405 | -32.7092 | -34.3578 | -36.0904 | -37.9112 | -39.8249 | -41.8361 | -43.9499 | -23.0307 | 0 | 0 | 0 | 0
| Project Terminal Value | Rs Cr | 170.3596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.3596 | 0 | 0 | 0 | 0
| Net Benefits | Rs Cr |  | -519.5723 | -477.9185 | 220.8226 | 220.01 | 219.1863 | 218.3497 | 217.4981 | 216.6295 | 215.7419 | 214.8329 | 213.9002 | 212.9415 | 211.9541 | 210.9352 | 209.8822 | 208.7919 | 207.6614 | 206.4872 | 205.2661 | 203.9943 | 202.6681 | 201.2835 | 199.8363 | 198.3221 | 196.7364 | 195.0742 | 289.2654 | 0 | 0 | 0 | 0
| Economic IRR | % | 19.49%
| Discount Factor (WACC) | % | 7.476%
| Project NPV | Rs Cr | 2259.5804

## Output
Project Assumptions | Units | FSP |  | Units | FSP |  |  | Capex Breakup | Rs per Wp | Rs Lakh /MW | Rs Crore
Project Assumptions |  |  | Capital Expenditure |  |  |  |  | Float Devices
Capacity | MWp | 243.888 | Capex | Rs Lakh | 121643.8843 | 4.9877 | 5.9852 | Floats and Platforms | 7.685 | 92.22 | 187.4279
Capacity | MW | 203.24 | IDC | Rs Lakh | 2612.319 | 0.10711 | 0.12853 | IT Platform | 2.802 | 33.63 | 68.3496
CUF | % | 19.32% | Capex including IDC | Rs Lakh | 124256.2032 | 5.0948 | 6.1138 | Anchor and Mooring | 4.878 | 58.53 | 118.9564
COD | Date | 2026-10-01 | [5 empty] | Float Devices | 15.365 | 184.38 | 374.7339
Life of Project | Years | 25 | Funding |  |  |  |  | Solar PV System
Funding Assumptions |  |  | Commerical Loan 1 | Rs Lakh | 86979.3423 |  |  | PV Module | 18.07 | 216.85 | 440.7259
Commerical Loan 1 | % | 70% | Commerical Loan 2 | Rs Lakh | 0 |  |  | Inverter (including switchgear) | 1.24 | 14.84 | 30.1608
Commerical Loan 2 | % | 0% | Grant/ Capital Subsidy | Rs Lakh | 0 |  |  | Balance of System (BoS) | 4.52 | 54.28 | 110.3187
Grant/ Capital Subsidy | % | 0% | Equity | Rs Lakh | 37276.861 |  |  | Civil Structure | 0.78 | 9.31 | 18.9216
Equity | % | 30% | Total Financing | Rs Lakh | 124256.2032 |  |  | PV System | 24.61 | 295.28 | 600.1271
Debt Assumptions |  |  | Levelized Tariff |  |  |  |  | Infrastructure
Moratorium Period (from start of operations) | Years | 0 | Generation O&M | Rs/kWh | 0.62716 |  |  | Land and Site Development | 0.73 | 8.72 | 17.7225
Repayment Period | Years | 15 | Infrastructure O&M | Rs/kWh | 0.11342 |  |  | Road Infrastructure | 0.04 | 0.43 | 0.87393
Interest Rate | % | 6% | Depreciation | Rs/kWh | 1.6265 |  |  | Infrastructure | 0.77 | 9.15 | 18.5965
|  |  | Interest on Term Loan | Rs/kWh | 0.74265 |  |  | Evacuation System
Return Assumption |  |  | Interest on WC | Rs/kWh | 0.071544 |  |  | Sub-station | 3.72 | 44.67 | 90.7873
Return on Equity (RoE) - Post Tax | % | 14% | ROE | Rs/kWh | 2.0722 |  |  | Transmission Line | 0.55 | 6.57 | 13.3529
|  |  | Project Tariff | Rs/kWh | 5.2536 |  |  | Augmentation | 0.2 | 2.45 | 4.9794
Working Capital Assumptions | [7 empty] | Evacuation System | 4.47 | 53.69 | 109.1196
Receivables | Months | 1.5 | Project Cost | Rs Cr/MW | 6.1138 |  |  | Other Costs
O&M | Months | 1 | Project IRR |  | 8.796% |  |  | Contingency, Insurance | 4.67 | 56.02 | 113.855
Maintenance spares | % | 15% | Equity IRR |  | 13.42% |  |  | IDC | 1.07 | 12.85 | 26.1163
Interest on WC | % | 11.5% | EIRR |  | 19.49% |  |  | Other Cost | 5.74 | 68.87 | 139.9714
|  |  | Discount Factor |  | 7.476% |  |  | Floating Solar Project Cost | 50.955 | 611.37 | 1242.5484
|  |  | Average DSCR |  | 2.2409

## Tables
[5 empty] | 85% | 12% | 13.8%
| Generation and Infrastructure BOQ |  | 5.2536
BOQ SPV
S.N | FPV plant | Unit | Quantity | Unit Cost (Rs./Unit) | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost (Rs. Lakhs) | Tax (Rs. Lakhs) | Total Cost (Rs. Lakhs) |  | Description | Total Cost (Rs Lakhs)
A | PV Modules | Lot | 421385 | 9187.2 | 32906.4603 | 4645.6179 | 38713.4827 | 5342.4606 | 44055.9433 |  | Land Cost | -
B | EL Testing | Lot | 1 | 1000000 | 8.5 | 1.2 | 10 | 1.38 | 11.38 |  | PV Module Cost | 44073.0133
C | Thermography | Lot | 1 | 500000 | 4.25 | 0.6 | 5 | 0.69 | 5.69 |  | Inverter Cost | 3016.269
| Grand Total |  |  |  | 32919.2103 | 4647.4179 | 38728.4827 | 5344.5306 | 44073.0133 |  | Floating Structure Cost | 37474.1815
[11 empty] | Electrical Infrastructure | 11031.3831
[11 empty] | Civil Infrastructure | 350.6569
[11 empty] | Road & Drainage Infrastructure | 1859.149
BOQ Inverter | [10 empty] | Water Infrastructure | 318.64
S.N | FPV plant | Unit | Quantity | Unit Cost (Rs./Unit) | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost (Rs. Lakhs) | Tax (Rs. Lakhs) | Total Cost (Rs. Lakhs) |  | Street-Light
A | Inverter 4.4 MW | Lot | 44 | 5700000 | 2131.8 | 300.96 | 2508 | 346.104 | 2854.104 |  | Cost of Power Evacuation
B | Inverter 1.1 MW | Lot | 12 | 1187500 | 121.125 | 17.1 | 142.5 | 19.665 | 162.165 |  | Statutory and Other Fees
| Grand Total |  |  |  | 2252.925 | 318.06 | 2650.5 | 365.769 | 3016.269 |  | Project Cost
Interest During Construction (IDC)
Total project cost
BOQ Floats
S.N | FPV plant | Unit | Quantity | Unit Cost (Rs./Unit) | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost (Rs. Lakhs) | Tax (Rs. Lakhs) | Total Cost (Rs. Lakhs)
A | Floating Structure
1 | OMF (Module Float) | Rs. Per Float | 420544 | 888.25 | 3735.4821 | 527.3622 | 4394.6848 | 606.4665 | 5001.1513
2 | OMWF (Main Walkway Float) | Rs. Per Float | 48032 | 3415.725 | 1640.641 | 231.6199 | 1930.1659 | 266.3629 | 2196.5288
3 | OLSF (Long Secondary Float) | Rs. Per Float | 163308 | 2049.435 | 3346.8913 | 472.5023 | 3937.5192 | 543.3776 | 4480.8968
4 | OSSF (Small Secondary Float) | Rs. Per Float | 148016 | 1366.29 | 2022.3278 | 285.5051 | 2379.2092 | 328.3309 | 2707.5401
5 | OSSFx (Small Secondary Walkway Float) | Rs. Per Float | 24096 | 6772.9062 | 1631.9995 | 230.3999 | 1919.9994 | 264.9599 | 2184.9593
6 | OCF (Cable Float)-DC | Rs. Per Float | 755372 | 107.3975 | 811.2506 | 114.5295 | 954.4125 | 131.7089 | 1086.1215
7 | OCF (Cable Float)-AC | Rs. Per Float | 905308 | 89.6325 | 811.4502 | 114.5577 | 954.6473 | 131.7413 | 1086.3886
| sub total |  |  |  | 14000.0426 | 1976.4766 | 16470.6383 | 2272.9481 | 18743.5864
B | Inverter Transformer Platform
1 | Transformer of Size 5.5 MVA | Rs. Per I.T. Platform | 12 | 4921712.5 | 590.6055 | 83.3796 | 694.83 | 95.8865 | 790.7165
2 | Transformer of Size 6.5 MVA | Rs. Per I.T. Platform | 32 | 5943200 | 1901.824 | 268.4928 | 2237.44 | 308.7667 | 2546.2067
3 | Platform-Ferro Cement | Lum Sum Cost | 52 | 4675000 | 2431 | 343.2 | 2860 | 394.68 | 3254.68
4 | Inverter Barge- Mooring Line length | Rs per KM | 11.88 | 1525510.0318 | 181.2306 | 25.5855 | 213.2125 | 29.4233 | 242.6358
| sub total |  |  |  | 5104.6601 | 720.6579 | 6005.4825 | 828.7566 | 6834.239
C | Anchoring & Mooring
1 | Mooring System | KM | 158.48 | 4996323.885 | 7918.1741 | 1117.8599 | 9315.4989 | 1285.5389 | 10601.0378
2 | Mooring Line Accessories | Lot | 2400 | 6379.25 | 153.102 | 21.6144 | 180.12 | 24.8566 | 204.9766
3 | Anchor System | Rs. Per Anchor | 5536 | 14711.035 | 814.4029 | 114.9745 | 958.1211 | 132.2207 | 1090.3418
| sub total |  |  |  | 8885.679 | 1254.4488 | 10453.74 | 1442.6161 | 11896.3561
| Grand Total |  |  |  | 27990.3816 | 3951.5833 | 32929.8607 | 4544.3208 | 37474.1815
BOQ Electrical
S.N | FPV plant | Unit | Quantity | Unit Cost (Rs./Unit) | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost (Rs. Lakhs) | Tax (Rs. Lakhs) | Total Cost (Rs. Lakhs)
A | DC BoS
1 | DC Cable | m | 1302246.4 | 58 | 642.0075 | 90.6363 | 755.3029 | 104.2318 | 859.5347
2 | DC Connectors | Lot | 1 | 26667745.3 | 266.6775 | 37.6486 | 313.7382 | 43.2959 | 357.034
3 | DC Accessories | Lot | 1 | 209388485.325 | 2093.8849 | 295.6073 | 2463.3939 | 339.9484 | 2803.3423
4 | String Monitoring Box | Lot | 1 | 46327125 | 463.2712 | 65.403 | 545.025 | 75.2135 | 620.2384
| sub total |  |  |  | 3465.841 | 489.2952 | 4077.46 | 562.6895 | 4640.1495
B | AC BoS
1 | AC Cables (1.9/3.3kV) - From Inverter - Inverter Transformer | Lot | 1 | 15643208.75 | 156.4321 | 22.0845 | 184.0377 | 25.3972 | 209.435
2 | Control Cable | m | 13120 | 120.4123 | 15.7981 | 2.2303 | 18.586 | 2.5649 | 21.1509
3 | Cable Tray | m | 340 | 329.5 | 1.1203 | 0.15816 | 1.318 | 0.18188 | 1.4999
4 | Perforated cable tray | Lot | 1 | 1189320 | 11.8932 | 1.679 | 13.992 | 1.9309 | 15.9229
5 | Hume Pipe | m | 6227.2 | 18.9063 | 1.1773 | 0.16621 | 1.3851 | 0.19114 | 1.5762
| sub total |  |  |  | 186.421 | 26.3183 | 219.3188 | 30.266 | 249.5849
D | Inverter Transformers, Switchgear and Panels
1 | Inverter Transformer | # | 46 | 4697391.0326 | 2160.7999 | 305.0541 | 2542.1175 | 350.8122 | 2892.9297
2 | HT Panels & RMU | # | 30 | 1452656.8 | 435.797 | 61.5243 | 512.7024 | 70.7529 | 583.4553
3 | HT Cables & Terminations | Lot | 1 | 62263180 | 622.6318 | 87.901 | 732.508 | 101.0861 | 833.5941
4 | LT System & Auxiliary System | # | 149 | 77070.4698 | 114.835 | 16.212 | 135.1 | 18.6438 | 153.7438
| sub total |  |  |  | 3334.0637 | 470.6913 | 3922.4279 | 541.2951 | 4463.723
E | Illumination System, Earthing
5 | Earthing System | Lot | 1 | 37267018.52 | 372.6702 | 52.6123 | 438.4355 | 60.5041 | 498.9396
6 | Lightning Protection with Earthing | Lot | 1 | 43861360 | 438.6136 | 61.9219 | 516.016 | 71.2102 | 587.2262
7 | Illumination System & Security System | Set | 2400 | 2833.3333 | 68 | 9.6 | 80 | 11.04 | 91.04
| sub total |  |  |  | 879.2838 | 124.1342 | 1034.4515 | 142.7543 | 1177.2058
F | SCADA & Master Control Room
1 | SCADA | Lot | 1 | 37400000 | 374 | 52.8 | 440 | 60.72 | 500.72
2 | Master Control Room | Lot | 1 | 0 | 0 | 0 | 0 | 0 | 0
| sub total |  |  |  | 374 | 52.8 | 440 | 60.72 | 500.72
| Grand Total |  |  |  | 8239.6096 | 1163.239 | 9693.6583 | 1337.7248 | 11031.3831
[7 empty] | 84002.5018 | 11592.3452 | 95594.847
BOQ Civil Infrastructure
S.N | FPV plant | Unit | Quantity | Unit Cost (Rs./Unit) | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost (Rs. Lakhs) | Tax (Rs. Lakhs) | Total Cost (Rs. Lakhs)
A | Building and Civil Infrastructure
1 | Master Control Room | sq ft | 15582 | 574.6 | 89.5342 | 12.6401 | 105.3343 | 14.5361 | 119.8705
2 | Offices | sq ft | 20000 | 574.6 | 114.92 | 16.224 | 135.2 | 18.6576 | 153.8576
3 | Common Infrastructure | sq ft | 10000 | 574.6 | 57.46 | 8.112 | 67.6 | 9.3288 | 76.9288
| Grand Total |  |  |  | 261.9142 | 36.9761 | 308.1343 | 42.5225 | 350.6569
BOQ Water Infrastructure
S.N | FPV plant | Unit | Quantity | Unit Cost (Rs./Unit) | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost (Rs. Lakhs) | Tax (Rs. Lakhs) | Total Cost (Rs. Lakhs)
A | Water Infrastructure
1 | Pier | # | 1 | 1700000 | 17 | 2.4 | 20 | 2.76 | 22.76
2 | Ferro Cement Launching Pads | # | 4 | 4250000 | 170 | 24 | 200 | 27.6 | 227.6
3 | Launch Pads | # | 6 | 850000 | 51 | 7.2 | 60 | 8.28 | 68.28
| Grand Total |  |  |  | 238 | 33.6 | 280 | 38.64 | 318.64
BOQ Others
S.N | FPV plant | Unit | Quantity | Unit Cost (Rs./Unit) | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost (Rs. Lakhs) | Tax (Rs. Lakhs) | Total Cost (Rs. Lakhs)
A | Other Infrastructure
1 | Lighting | # | 2000 | 2550 | 51 | 7.2 | 60 | 8.28 | 68.28
2 | Gates | # | 1 | 425000 | 4.25 | 0.6 | 5 | 0.69 | 5.69
3 | Green Belt | # | 1 | 850000 | 8.5 | 1.2 | 10 | 1.38 | 11.38
4 | Environment Mitigation Charges | # | 1 |  |  |  | 1000 | 138 | 1138
| Grand Total |  |  |  | 913.75 | 129 | 1075 | 148.35 | 1223.35
| Total Generation Cost |  |  |  | 72815.7907 | 10279.8763 | 85665.6361 | 11821.8578 | 97487.4939
BOQ Road Development and Drainage Infrastructure
S.N | FPV plant | Unit | Quantity | Unit Cost (Rs./Unit) | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost (Rs. Lakhs) | Tax (Rs. Lakhs) | Total Cost (Rs. Lakhs)
A | Road Development and Drainage Infrastructure
1 | Land and Site Development | # | 15.0205 | 8500000 | 1276.7425 | 180.246 | 1502.05 | 270.369 | 1772.419
2 | Access Road | KM | 0.6125 | 10200000 | 62.475 | 8.82 | 73.5 | 13.23 | 86.73
| Grand Total |  |  |  | 1339.2175 | 189.066 | 1575.55 | 283.599 | 1859.149
| Total Infrastructure Cost |  |  |  | 1339.2175 | 189.066 | 1575.55 | 283.599 | 1859.149
| Total Cost |  |  |  | 82014.6553 | 11578.5396 | 96487.8297 | 13769.8526 | 110257.6824
[7 empty] | 96488.3547 | 13769.9251 | 110258.2798
| Description | Total Cost (Rs Crore) | Cost Estimate
(Rs Crore/MW)
| Project cost | 1216.4388 | 5.9852
| Interest During Construction (IDC) | 26.1232 | 0.12853
| Total project cost | 1242.562 | 6.1138
| Date | PAT | Depreciation | Tax Shield | Finance Cost | Change in WC | Capex | Terminal Value | Cash Flow
| FY 26 | 0 | 0 | 0 | 0 | 0 | -582.0486 | 0 | -582.0486
| FY 27 | 28.4504 | 28.9343 | -3.3937 | 18.6722 | -25.6789 | -660.5135 | 0 | -612.4248
| FY 28 | 44.8522 | 58.0276 | -8.7356 | 48.7084 | 0.19361 | 0 | 0 | 145.2444
| FY 29 | 45.3175 | 58.0276 | -8.1369 | 45.2293 | 0.11121 | 0 | 0 | 142.7372
| FY 30 | 45.7751 | 58.0276 | -7.5384 | 41.7501 | 0.099367 | 0 | 0 | 140.2937
| FY 31 | 46.2232 | 58.0276 | -6.9401 | 38.2709 | 0.087135 | 0 | 0 | 137.8412
| FY 32 | 46.6599 | 58.0276 | -6.3419 | 34.7917 | 0.074495 | 0 | 0 | 135.3778
| FY 33 | 47.0832 | 58.0276 | -5.744 | 31.3126 | 0.061424 | 0 | 0 | 132.9015
| FY 34 | 47.491 | 58.0276 | -5.1463 | 27.8334 | 0.047898 | 0 | 0 | 130.4103
| FY 35 | 47.8812 | 58.0276 | -4.5488 | 24.3542 | 0.033889 | 0 | 0 | 127.9019
| FY 36 | 48.2515 | 58.0276 | -3.9514 | 20.875 | 0.019371 | 0 | 0 | 125.3741
| FY 37 | 48.5996 | 58.0276 | -3.3543 | 17.3959 | 0.0043145 | 0 | 0 | 122.8247
| FY 38 | 48.9229 | 58.0276 | -2.7575 | 13.9167 | -0.011311 | 0 | 0 | 120.251
| FY 39 | 49.2189 | 58.0276 | -2.1609 | 10.4375 | -0.027536 | 0 | 0 | 117.6506
| FY 40 | 49.485 | 58.0276 | -1.5645 | 6.9583 | -0.044395 | 0 | 0 | 115.0208
| FY 41 | 49.7182 | 58.0276 | -0.96839 | 3.4792 | -0.061924 | 0 | 0 | 112.3589
| FY 42 | 76.6785 | 24.8512 | -0.52181 | 0.86979 | -0.080158 | 0 | 0 | 103.9687
| FY 43 | 74.6756 | 24.8512 | -0.37402 | 0 | -0.099138 | 0 | 0 | 101.2333
| FY 44 | 71.9102 | 24.8512 | -0.37578 | 0 | -0.1189 | 0 | 0 | 98.4566
| FY 45 | 69.0993 | 24.8512 | -0.37784 | 0 | -0.1395 | 0 | 0 | 95.6351
| FY 46 | 65.5989 | 24.8512 | -0.39798 | 0 | -0.16096 | 0 | 0 | 92.107
| FY 47 | 54.1599 | 24.8512 | -0.65055 | 0 | -0.18335 | 0 | 0 | 80.4088
| FY 48 | 51.3645 | 24.8512 | -0.66366 | 0 | -0.20671 | 0 | 0 | 77.5948
| FY 49 | 48.512 | 24.8512 | -0.67854 | 0 | -0.23109 | 0 | 0 | 74.723
| FY 50 | 45.5985 | 24.8512 | -0.69548 | 0 | -0.25655 | 0 | 0 | 71.7892
| FY 51 | 42.6198 | 24.8512 | -0.71487 | 0 | -0.28315 | 0 | 0 | 68.789
| FY52 | 28.8444 | 12.4256 | -0.37269 | 0 | -3.2061 | 0 | 170.3596 | 206.2406
8.796%
| Date | Replacement of Energy (in MU) | Cost of using Fossil Fuel (in Rs. Cr) | Cost of using Non- Fossil Fuel (in Rs. Crore) | Net Savings (in Rs. Crore)
|  | (A) | (B) | (C) | [D=(B-C)]
| FY 27 | 170.9605 | 69.0628 | 89.815 | -20.7522
| FY 29 | 337.5083 | 139.0698 | 177.3117 | -38.2419
| FY 30 | 333.2894 | 140.0781 | 175.0953 | -35.0172
| FY 31 | 329.1233 | 141.0937 | 172.9066 | -31.813
| FY 32 | 325.0093 | 142.1166 | 170.7453 | -28.6287
| FY 33 | 320.9467 | 143.1469 | 168.611 | -25.4641
| FY 34 | 316.9348 | 144.1847 | 166.5034 | -22.3186
| FY 35 | 312.9732 | 145.2301 | 164.4221 | -19.192
| FY 36 | 309.061 | 146.283 | 162.3668 | -16.0838
| FY 37 | 305.1977 | 147.3436 | 160.3372 | -12.9937
| FY 38 | 301.3828 | 148.4118 | 158.333 | -9.9212
| FY 39 | 297.6155 | 149.4878 | 156.3538 | -6.866
| FY 40 | 293.8953 | 150.5716 | 154.3994 | -3.8278
| FY 41 | 290.2216 | 151.6632 | 152.4694 | -0.8062
| FY 42 | 286.5938 | 152.7628 | 150.5635 | 2.1992
| FY 43 | 283.0114 | 153.8703 | 148.6815 | 5.1888
| FY 44 | 279.4738 | 154.9859 | 146.823 | 8.1629
| FY 45 | 275.9803 | 156.1095 | 144.9877 | 11.1218
| FY 46 | 272.5306 | 157.2413 | 143.1753 | 14.066
| FY 47 | 269.1239 | 158.3813 | 141.3857 | 16.9956
| FY 48 | 265.7599 | 159.5296 | 139.6183 | 19.9112
| FY 49 | 262.4379 | 160.6862 | 137.8731 | 22.813
| FY 50 | 259.1574 | 161.8511 | 136.1497 | 25.7014
| FY 51 | 255.918 | 163.0245 | 134.4478 | 28.5767
| FY 52 | 252.719 | 164.2065 | 132.7672 | 31.4393
|  | 147.019 | 96.4775 | 77.2372 | 19.2403
Cumulative Savings due to Non-Use of Fossil Fuel in 25 years is
-66.5102
Transmission BOQ
Transmission Line and Sub-station
| Summary | Particulars | Unit Price | Quantity | Unit Rate | Equipment Cost (Rs. Lakhs) | Erection Cost (Rs. Lakhs) | Base Cost | Tax | Lumpsum Cost
|  | Pooling Sub-Station - 300 MW, 33/220 KV | [5 empty] | INR Lakhs | INR Lakhs | INR Lakhs
| 1 | 33/220 kV, 80 MVA Power Transformer | Lakhs/# | 4 | 1321.984 | 4494.7456 | 114.2194 | 5287.936 | 951.8285 | 6239.7645
| 2 | 33kV Incomer Feeder Bays (25MW) to 33 kV Bus | Lakhs/# | 12 | 20.534 | 209.4468 | 5.3224 | 246.408 | 44.3534 | 290.7614
| 3 | 33 kV Bus Section & Bus Coupler Bays | Lakhs/# | 8 | 13.0231 | 88.5572 | 2.2504 | 104.185 | 18.7533 | 122.9383
| 4 | 33kV incoming feeders for Power transformer | Lakhs/# | 4 | 19.83 | 67.422 | 1.7133 | 79.32 | 14.2776 | 93.5976
| 5 | Reactive Power Compensation as per CEA connectivity standard, | Lakhs/MVAr | 60 | 20.5915 | 1050.1665 | 26.6866 | 1235.49 | 222.3882 | 1457.8782
| 6 | 220kV Power Transformer Bay | Lakhs/# | 4 | 41.548 | 141.2632 | 3.5897 | 166.192 | 29.9146 | 196.1066
| 7 | 220 kV Line Bay+ Bus Coupler Bay | Lakhs/# | 3 | 41.548 | 105.9474 | 2.6923 | 124.644 | 22.4359 | 147.0799
| 8 | 220 kV Bus Transfer Bay | Lakhs/# | 1 | 41.548 | 35.3158 | 0.89744 | 41.548 | 7.4786 | 49.0266
| 9 | Control & Communication | Lakhs/# | 1 | 408.01 | 346.8085 | 8.813 | 408.01 | 73.4418 | 481.4518
| A | Pooling Sub-station |  |  |  | 6539.6731 | 923.248 | 7693.733 | 1384.8719 | 9078.6049
Transmission Line
Transmission Line Supply of Material as per specifications
| 1 | Supply of 220kV Towers including fasteners | Lakhs/Lot | 4 | 35.1322 | 140.5287 | 3.5711 | 165.3279 | 29.759 | 195.087
| 2 | ACCC Conductor, Earthwire Conductor & Accessories | Lakhs/Lot | 4 | 102.3099 | 409.2397 | 10.3995 | 481.4585 | 86.6625 | 568.121
| 3 | 220 KV Insulator with Stringing Accessories | Lakhs/Lot | 4 | 3.3726 | 13.4905 | 0.34282 | 15.8712 | 2.8568 | 18.728
| 4 | 220kV Tower Earthing | Lakhs/Lot | 4 | 0.34272 | 1.3709 | 0.034836 | 1.6128 | 0.2903 | 1.9031
| 5 | 220kV Tower Accessories | Lakhs/Lot | 4 | 0.32713 | 1.3085 | 0.033252 | 1.5394 | 0.2771 | 1.8165
Transmission Line Services & Erection Activities
| 1 | Survey and Field Assessment | Lakhs/Lot | 1 | 1.8972 | 1.8972 | 0.048211 | 2.232 | 0.40176 | 2.6338
| 2 | Tower Foundation and Errection | Lakhs/Lot | 1 | 136.0117 | 136.0117 | 3.4563 | 160.0138 | 28.8025 | 188.8163
| 3 | Mounting of Insulators and Stringing | Lakhs/Lot | 1 | 26.996 | 26.996 | 0.68602 | 31.76 | 5.7168 | 37.4768
| 4 | Earthing of transmission towers: | Lakhs/Lot | 1 | 0.714 | 0.714 | 0.018144 | 0.84 | 0.1512 | 0.9912
| 5 | ROW / Crop & Land Compensation | Lakhs/Lot | 1 | 90.78 | 90.78 | 2.3069 | 106.8 | 19.224 | 126.024
| 6 | Centage charges | Lakhs/Lot | 1 | 28.2969 | 28.2969 | 0.71907 | 33.2905 | 5.9923 | 39.2828
| 7 | Erection Charges | Lakhs/Lot | 1 | 110.5825 | 110.5825 | 2.8101 | 130.097 | 23.4175 | 153.5145
| B | Transmission Line System |  | 1 |  | 961.2167 | 135.7012 | 1130.8432 | 203.5518 | 1334.3949
Augmentation Work @ BkTPS Substation
| 1 | 220 kV Line Bay+ Bus Section Bay | Lakhs/Lot | 2 | 42.778 | 72.7226 | 1.848 | 85.556 | 15.4001 | 100.9561
| 2 | EHV Cabling | Lakhs/Mtr | 300 | 0.64764 | 165.1482 | 4.1967 | 194.292 | 34.9726 | 229.2646
| 3 | Miscellaneous (Control and Protection) | Lakhs/No. | 1 | 142.2195 | 120.8866 | 3.0719 | 142.2195 | 25.5995 | 167.819
| C | Augmentation Works |  |  |  | 358.7574 | 50.6481 | 422.0675 | 75.9721 | 498.0396
|  | Total Transmission Cost |  |  |  | 7859.6471 | 1109.5972 | 9246.6437 | 1664.3959 | 10911.0395
| Description | Base Cost (Rs Lakhs) | Tax | Total Cost (Rs Lakhs)
(Rs Lakhs)
Land Cost
| PV Module Cost | 38728.4827 | 5344.5306 | 44073.0133
| Inverter Cost | 2650.5 | 365.769 | 3016.269
| Floating Structure Cost | 32929.8607 | 4544.3208 | 37474.1815
| Electrical Infrastructure | 9693.6583 | 1337.7248 | 11031.3831
| Civil Infrastructure | 308.1343 | 42.5225 | 350.6569
| Road & Drainage Infrastructure | 1575.55 | 283.599 | 1859.149
| Water Infrastructure | 280 | 38.64 | 318.64
| Other Infrastructure | 1075 | 148.35 | 1223.35
| Cost of Power Evacuation | 9246.6437 | 1664.3959 | 10911.0395
| Statutory and Other Fees |  |  | 11385.6044
| Project Cost |  |  | 121643.2868
| Interest During Construction (IDC) |  |  | 2612.319
| Total project cost |  |  | 124255.6058
Statutory and Other Fees
| S.N | FPV plant | Total Cost (Rs. Lakhs)
| 1 | Generation | 10753.6304
| 2 | Transmission | 386.2508
| 3 | Others | 245.7232
|  | Grand Total | 11385.6044

## Assumptions
ASSUMPTION TABLE
Project Particulars |  |  | Operational Details of the Project
Installed Capacity of the plant | MWp | 243.888 | Capacity Utilization Factor | % | 19.32%
Start of the Project | Date | 2025-04-01 | Annual Degradation (3rd Year Onwards) | % | 0.5%
Construction Period | Months | 18 | Aux Consumption | % | 0.75%
Start of Operations | Date | 2026-10-01
First Operational Financial Year | Date | 2027-03-31 | Depreciation Assumption
Project Life | Months | 25 | Normative Life of Project | Years | 25
Project End Date | Date | 2052-03-31 | Depreciation Rate (1st 13 years) | % | 4.67%
|  |  | Depreciation Rate (After 13 Years) | % | 2%
Financing Details
Project Cost | INR Cr | 1242.562 | Tax Assumption
Loan | % | 70% | Income Tax Rate | % | 22%
Equity | % | 30%
Grant | % | 0% | Working Capital Assumption
Moratorium Period | Years | 0 | O&M Expenses (including GST) | Lakhs/MW/year | 5.4988
Repayment Period | Years | 15 | O&M Expenses Escalation | % | 5.25%
Interest Rate | % | 6% | Maintenance Spares | % | 15%
Return on Equity | % | 14% | Receivables | Months | 1.5
|  |  | Interest on Working Capital | % | 11.5%
|  |  | Working Capital Margin | % | 25%
Levelized Tariff Calculation
|  |  | Discounting Factor | % | 7.476%
|  |  | Levelized Tariff | INR/KWh | 5.2536

## Tariff
Particulars | Units | Inputs | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
|  | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31 | 2031-03-31 | 2032-03-31 | 2033-03-31 | 2034-03-31 | 2035-03-31 | 2036-03-31 | 2037-03-31 | 2038-03-31 | 2039-03-31 | 2040-03-31 | 2041-03-31 | 2042-03-31 | 2043-03-31 | 2044-03-31 | 2045-03-31 | 2046-03-31 | 2047-03-31 | 2048-03-31 | 2049-03-31 | 2050-03-31 | 2051-03-31 | 2052-03-31
Total Year Counter |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
Is Operational ? | 26 |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Operational Year Number |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
Days in year |  |  | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366
Days of Construction |  |  | 0: 365; 1: 183; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0
Days in Operations |  |  | 0 | 182 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 183
Proportion of year in operation |  |  | 0 | 0.49863 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5
Cumulative number of year in operation |  |  | 0 | 0.49863 | 1.4986 | 2.4986 | 3.4986 | 4.4986 | 5.4986 | 6.4986 | 7.4986 | 8.4986 | 9.4986 | 10.4986 | 11.4986 | 12.4986 | 13.4986 | 14.4986 | 15.4986 | 16.4986 | 17.4986 | 18.4986 | 19.4986 | 20.4986 | 21.4986 | 22.4986 | 23.4986 | 24.4986 | 24.9986
Energy Generation Computation
Capacity | MW | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24
Degradation | % | 0% | 0% | 0.2493% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.25%
Effective capacity | MW | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24 | 203.24
CUF | % | 19.32% | 0% | 19.26% | 18.91% | 18.72% | 18.49% | 18.26% | 17.98% | 17.8% | 17.58% | 17.36% | 17.1% | 16.93% | 16.72% | 16.51% | 16.26% | 16.1% | 15.9% | 15.7% | 15.46% | 15.31% | 15.12% | 14.93% | 14.7% | 14.56% | 14.37% | 14.19% | 16.47%
Net Saleable Energy | MU | 343.931 | 0 | 170.9605 | 337.5083 | 333.2894 | 329.1233 | 325.0093 | 320.9467 | 316.9348 | 312.9732 | 309.061 | 305.1977 | 301.3828 | 297.6155 | 293.8953 | 290.2216 | 286.5938 | 283.0114 | 279.4738 | 275.9803 | 272.5306 | 269.1239 | 265.7599 | 262.4379 | 259.1574 | 255.918 | 252.719 | 147.019
Fixed Charge Computation
Generation O&M | Rs Cr |  | 0 | 5.5726 | 11.7625 | 12.38 | 13.03 | 13.714 | 14.434 | 15.1918 | 15.9894 | 16.8288 | 17.7123 | 18.6422 | 19.621 | 20.6511 | 21.7352 | 22.8763 | 24.0773 | 25.3414 | 26.6718 | 28.0721 | 29.5459 | 31.0971 | 32.7296 | 34.448 | 36.2565 | 38.1599 | 20.0817
Infrastructure O&M | Rs Cr |  | 0 | 1.1878 | 2.4719 | 2.5651 | 2.6618 | 2.7621 | 2.8663 | 2.9743 | 3.0864 | 3.2028 | 3.3235 | 3.4488 | 3.5789 | 3.7138 | 3.8538 | 3.9991 | 4.1499 | 4.3063 | 4.4687 | 4.6371 | 4.8119 | 4.9933 | 5.1816 | 5.3769 | 5.5797 | 5.79 | 2.9491
Depreciation | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256
Interest on Term Loan | Rs Cr |  | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest on WC | Rs Cr |  | 0 | 1.1044 | 2.1981 | 2.1885 | 2.1799 | 2.1724 | 2.166 | 2.1607 | 2.1566 | 2.1537 | 2.152 | 2.1516 | 2.1526 | 2.155 | 2.1588 | 2.1641 | 2.171 | 2.1796 | 2.1899 | 2.2019 | 2.2158 | 2.2316 | 2.2494 | 2.2693 | 2.2915 | 2.3159 | 1.2962
Total Cost | Rs Cr |  |  | 55.4713 | 123.1686 | 120.3905 | 117.6494 | 114.9472 | 112.2857 | 109.667 | 107.0934 | 104.5671 | 102.0906 | 99.6662 | 97.2968 | 94.985 | 92.7338 | 90.5464 | 56.1193 | 56.6786 | 58.1816 | 59.7623 | 61.4248 | 63.1732 | 65.0119 | 66.9455 | 68.9788 | 71.1171 | 36.7526
ROE | Rs Cr |  | 0 | 31.4127 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 62.9981 | 66.9072 | 66.9072 | 66.9072 | 66.9072 | 66.9072 | 33.4536
Total ARR | Rs Cr |  | 0 | 86.884 | 186.1666 | 183.3886 | 180.6475 | 177.9452 | 175.2837 | 172.6651 | 170.0915 | 167.5652 | 165.0886 | 162.6643 | 160.2948 | 157.9831 | 155.7319 | 153.5445 | 119.1174 | 119.6766 | 121.1797 | 122.7604 | 124.4229 | 130.0804 | 131.9191 | 133.8527 | 135.886 | 138.0243 | 70.2062
Per Unit Cost
Generation O&M | Rs/kWh |  |  | 0.32596 | 0.34851 | 0.37145 | 0.3959 | 0.42196 | 0.44973 | 0.47934 | 0.51089 | 0.54451 | 0.58036 | 0.61856 | 0.65927 | 0.70267 | 0.74892 | 0.79821 | 0.85076 | 0.90675 | 0.96644 | 1.0301 | 1.0979 | 1.1701 | 1.2471 | 1.3292 | 1.4167 | 1.51 | 1.3659
Infrastructure O&M | Rs/kWh |  |  | 0.069477 | 0.073239 | 0.076962 | 0.080875 | 0.084986 | 0.089306 | 0.093846 | 0.098617 | 0.10363 | 0.1089 | 0.11443 | 0.12025 | 0.12636 | 0.13279 | 0.13954 | 0.14663 | 0.15409 | 0.16192 | 0.17015 | 0.1788 | 0.18789 | 0.19744 | 0.20748 | 0.21803 | 0.22911 | 0.20059
Depreciation | Rs/kWh |  |  | 1.6925 | 1.7193 | 1.7411 | 1.7631 | 1.7854 | 1.808 | 1.8309 | 1.8541 | 1.8775 | 1.9013 | 1.9254 | 1.9498 | 1.9744 | 1.9994 | 2.0247 | 0.8781 | 0.88922 | 0.90047 | 0.91187 | 0.92341 | 0.9351 | 0.94694 | 0.95892 | 0.97106 | 0.98335 | 0.84517
Interest on Term Loan | Rs/kWh |  |  | 1.0922 | 1.4432 | 1.3571 | 1.2685 | 1.1775 | 1.084 | 0.98798 | 0.88932 | 0.78801 | 0.68398 | 0.5772 | 0.46761 | 0.35514 | 0.23976 | 0.1214 | 0.030734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest on WC | Rs/kWh |  |  | 0.064598 | 0.065128 | 0.065664 | 0.066235 | 0.066842 | 0.067488 | 0.068175 | 0.068906 | 0.069684 | 0.070511 | 0.071391 | 0.072328 | 0.073324 | 0.074384 | 0.075512 | 0.076712 | 0.077989 | 0.079348 | 0.080794 | 0.082333 | 0.08397 | 0.085712 | 0.087566 | 0.089539 | 0.091639 | 0.088166
ROE | Rs/kWh |  |  | 1.8374 | 1.8666 | 1.8902 | 1.9141 | 1.9383 | 1.9629 | 1.9877 | 2.0129 | 2.0384 | 2.0642 | 2.0903 | 2.1168 | 2.1436 | 2.1707 | 2.1982 | 2.226 | 2.2542 | 2.2827 | 2.3116 | 2.3409 | 2.5176 | 2.5494 | 2.5817 | 2.6144 | 2.6475 | 2.2755
Year on Year Tariff | Rs/kWh |  |  | 5.0821 | 5.5159 | 5.5024 | 5.4887 | 5.4751 | 5.4615 | 5.448 | 5.4347 | 5.4218 | 5.4092 | 5.3973 | 5.386 | 5.3755 | 5.366 | 5.3576 | 4.2089 | 4.2822 | 4.3909 | 4.5045 | 4.6233 | 4.8947 | 5.0267 | 5.1649 | 5.3097 | 5.4616 | 4.7753
Discounting Factor |  |  |  | 1 | 0.93044 | 0.86572 | 0.8055 | 0.74947 | 0.69734 | 0.64883 | 0.6037 | 0.5617 | 0.52263 | 0.48628 | 0.45245 | 0.42098 | 0.3917 | 0.36445 | 0.3391 | 0.31551 | 0.29357 | 0.27314 | 0.25415 | 0.23647 | 0.22002 | 0.20471 | 0.19047 | 0.17722 | 0.1649
Levelized Tariff | Rs/kWh | 5.2536

## IDC_Q
| Particulars | Units | Inputs | 2025-04-01 | 2025-07-01 | 2025-10-01 | 2026-01-01 | 2026-04-01 | 2026-07-01 | 2026-10-01 | 2027-01-01 | 2027-04-01 | 2027-07-01 | 2027-10-01 | 2028-01-01 | 2028-04-01 | 2028-07-01 | 2028-10-01 | 2029-01-01 | 2029-04-01 | 2029-07-01 | 2029-10-01 | 2030-01-01 | 2030-04-01 | 2030-07-01 | 2030-10-01 | 2031-01-01 | 2031-04-01 | 2031-07-01 | 2031-10-01 | 2032-01-01 | 2032-04-01 | 2032-07-01 | 2032-10-01 | 2033-01-01 | 2033-04-01
|  |  | 2025-03-31 | 2025-06-30 | 2025-09-30 | 2025-12-31 | 2026-03-31 | 2026-06-30 | 2026-09-30 | 2026-12-31 | 2027-03-31 | 2027-06-30 | 2027-09-30 | 2027-12-31 | 2028-03-31 | 2028-06-30 | 2028-09-30 | 2028-12-31 | 2029-03-31 | 2029-06-30 | 2029-09-30 | 2029-12-31 | 2030-03-31 | 2030-06-30 | 2030-09-30 | 2030-12-31 | 2031-03-31 | 2031-06-30 | 2031-09-30 | 2031-12-31 | 2032-03-31 | 2032-06-30 | 2032-09-30 | 2032-12-31 | 2033-03-31
| Is Operational ? | 25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Operational Quarter Number |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| Days in Quarter |  |  | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 91 | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 91 | 91 | 92 | 92 | 90
| Year No. |  | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8
| Days in Operations |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 90 | 91 | 92 | 92 | 91 | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 91 | 91 | 92 | 92 | 90
| Days in Construction |  |  | 91 | 92 | 92 | 90 | 91 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Proportion of year in operation |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Cumulative number of year in operation |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
CapEX
| Capacity of the Project | MW | 203.24 | 0: MWp; 0: 243.888
| Generation Project | Unit | Unit Cost | 0: Quantity; 0: Cost (Rs Lakh); 0: Tax; 0: Total Cost
II | Capital Expenditure - Generation | bar: 0 to 0
A | SPV Modules | Lot | 159 | 0: 243.888; 0: 38728.4827; 0: 5344.5306; 0: 44073.0133
B | Inverters | Lot | 13 | 0: 203.24; 0: 2650.5; 0: 365.769; 0: 3016.269
C | Floating Structure for Module and inverters | Lot | 135 | 0: 243.888; 0: 32929.8607; 0: 4544.3208; 0: 37474.1815
D | Balance of Plant (Cables, SCB, Accessories) | Lot | 40 | 0: 243.888; 0: 9694.1833; 0: 1337.7973; 0: 11031.9806
E | Civil Structure | Lot | 7 | 0: 243.888; 0: 1663.1343; 0: 229.5125; 0: 1892.6469
| Capital Expenditure - Generation | Lot |  | 0: 85666.1611; 0: 11821.9302; 0: 97488.0913
III | Capital Expenditure - Transmission Evacuation | bar: 0 to 0
A | Pooling Sub-station | MVA | 24.0429 | 0: 320; 0: 7693.733; 0: 1384.8719; 0: 9078.6049
B | Transmission Line System | kM | 282.7108 | 0: 4; 0: 1130.8432; 0: 203.5518; 0: 1334.3949
C | Augmentation Works | Lot | 422.0675 | 0: 1; 0: 422.0675; 0: 75.9721; 0: 498.0396
| Capital Expenditure - Transmission Evacuation | Lot |  | 0: 9246.6437; 0: 1664.3959; 0: 10911.0395
I | Capital Expenditure - Infrastructure | bar: 0 to 0
A | Land & Site Development | Lot | 0 | 0: 0; 0: 1502.05; 0: 270.369; 0: 1772.419
C | Road Infrastructure | Lot | 0 | 0: 0; 0: 73.5; 0: 13.23; 0: 86.73
| Capital Expenditure - Infrastructure | Lot |  | 0: 1575.55; 0: 283.599; 0: 1859.149
IV | Capital Expenditure - Other Costs | bar: 0 to 0
A | Generation (Contingency, Insurance, Warranty, etc) | Lot | 0 | 0: 0; 0: 9449.5874; 0: 1304.0431; 0: 10753.6304
B | Transmission (Contingency, Insurance, Warranty, etc) | Lot | 0 | 0: 0; 0: 327.3312; 0: 58.9196; 0: 386.2508
C | Other Charges/Statutory Charges | Lot | 0 | 0: 0; 0: 208.24; 0: 37.4832; 0: 245.7232
| Capital Expenditure - Other Costs | Lot |  | 0: 9985.1586; 0: 1400.4459; 0: 11385.6044
[6 empty] | 15170.371 | 121643.8843
| Interest During Construction | Lot |  | 0: 2612.319
| Grand Total | Lot |  | 0: 0; 0: 15170.371; 0: 124256.2032
Capital Cost without IDC | bar: 0 to 0
1 | Capital Expenditure - Generation & Transmission | Rs Cr |  | 0: 949.128; 0: 134.8633; 0: 1083.9913
2 | Capital Expenditure - Infrastructure | Rs Cr |  | 0: 15.7555; 0: 2.836; 0: 18.5915
3 | Capital Expenditure - Other Costs | Rs Cr |  | 0: 99.8516; 0: 14.0045; 0: 113.856
| Capital Cost - Total | Rs Cr |  | 0: 1064.7351; 0: 151.7037; 0: 1216.4388
| Interest During Construction | Rs Cr |  | 0: 26.1232
| Gross Capital Cost | Rs Cr |  | 0: 1242.562
Phasing |  | Rs Cr
1 | Capital Expenditure - Generation & Transmission | Rs Cr | 1083.9913 | 0 | 38.0753 | 113.5855 | 408.2725 | 436.3831 | 87.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital Expenditure - Infrastructure |  | 18.5915 | 0 | 0 | 2.7887 | 2.7887 | 6.507 | 6.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Capital Expenditure - Other Costs | Rs Cr | 113.856 | 0 | 0 | 5.6928 | 5.6928 | 51.2352 | 51.2352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phasing - Capex | Rs Cr | 1216.4388 | 0 | 38.0753 | 122.067 | 416.754 | 494.1253 | 145.4172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IDC | Rs Cr | 26.1232 | 0 | 0.20095 | 1.0483 | 3.9031 | 8.7516 | 12.2193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capex incl. IDC | Rs Cr | 1242.562 | 0 | 38.2762 | 123.1152 | 420.6571 | 502.877 | 157.6365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commerical Loan 1 | % |  | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70%
| Commercial Loan 2 | % | bar: 0 to 25
| Grant | % | bar: 0 to 25
| Equity | % |  | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30%
| Commerical Loan 1 | Rs Cr | 869.7934 | 0 | 26.7934 | 86.1807 | 294.46 | 352.0139 | 110.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commerical Loan 2 | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grant | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equity | Rs Cr | 372.7686 | 0 | 11.4829 | 36.9346 | 126.1971 | 150.8631 | 47.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Grant Schedule
| Grant | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cumulative Grant | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Equity Schedule
| Equity | Rs Cr |  | 0 | 11.4829 | 36.9346 | 126.1971 | 150.8631 | 47.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cumulative Equity | Rs Cr |  | 0 | 11.4829 | 48.4174 | 174.6146 | 325.4777 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686
Commerical Loan 1 Schedule
| Opening | Rs Cr |  | 0 | 0 | 26.7934 | 112.974 | 407.434 | 759.4479 | 869.7934 | 855.2969 | 840.8003 | 826.3038 | 811.8072 | 797.3106 | 782.8141 | 768.3175 | 753.821 | 739.3244 | 724.8279 | 710.3313 | 695.8347 | 681.3382 | 666.8416 | 652.3451 | 637.8485 | 623.352 | 608.8554 | 594.3588 | 579.8623 | 565.3657 | 550.8692 | 536.3726 | 521.8761
| Drawdown | Rs Cr | 869.7934 | 0 | 26.7934 | 86.1807 | 294.46 | 352.0139 | 110.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repayments | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966 | 14.4966
| Closing | Rs Cr |  | 0 | 26.7934 | 112.974 | 407.434 | 759.4479 | 869.7934 | 855.2969 | 840.8003 | 826.3038 | 811.8072 | 797.3106 | 782.8141 | 768.3175 | 753.821 | 739.3244 | 724.8279 | 710.3313 | 695.8347 | 681.3382 | 666.8416 | 652.3451 | 637.8485 | 623.352 | 608.8554 | 594.3588 | 579.8623 | 565.3657 | 550.8692 | 536.3726 | 521.8761 | 507.3795
| Interest Rate | % | bar: 0 to 25
| IDC | Rs Cr | 26.1232 | 0 | 0.20095 | 1.0483 | 3.9031 | 8.7516 | 12.2193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Charge | Rs Cr | 937.6373 | 0 | 0 | 0 | 0 | 0 | 0 | 51.7527 | 50.8829 | 50.0131 | 49.1433 | 48.2735 | 47.4037 | 46.5339 | 45.6642 | 44.7944 | 43.9246 | 43.0548 | 42.185 | 41.3152 | 40.4454 | 39.5756 | 38.7058 | 37.836 | 36.9662 | 36.0964 | 35.2266 | 34.3568 | 33.487 | 32.6173 | 31.7475 | 30.8777
Commercial Loan 2 Schedule
| Opening | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Addition | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repayments | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Rate | % |  | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
| IDC | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Charge | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FS
| Particulars | Units | Inputs | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
|  |  | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31 | 2031-03-31 | 2032-03-31 | 2033-03-31 | 2034-03-31 | 2035-03-31 | 2036-03-31 | 2037-03-31 | 2038-03-31 | 2039-03-31 | 2040-03-31 | 2041-03-31 | 2042-03-31 | 2043-03-31 | 2044-03-31 | 2045-03-31 | 2046-03-31 | 2047-03-31 | 2048-03-31 | 2049-03-31 | 2050-03-31 | 2051-03-31 | 2052-03-31
| Total Year Counter |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
| Is Operational ? | 26 |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Operational Year Number |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| Days in year |  |  | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366
| Days of Construction |  |  | 0: 365; 1: 183; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0
| Days in Operations |  |  | 0 | 182 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 183
Financial Statements & IRR
P&L Account
| Revenue | Rs Cr | 0 | 0 | 89.815 | 177.3117 | 175.0953 | 172.9066 | 170.7453 | 168.611 | 166.5034 | 164.4221 | 162.3668 | 160.3372 | 158.333 | 156.3538 | 154.3994 | 152.4694 | 150.5635 | 148.6815 | 146.823 | 144.9877 | 143.1753 | 141.3857 | 139.6183 | 137.8731 | 136.1497 | 134.4478 | 132.7672 | 77.2372
| Expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generation O&M | Rs Cr | 0 | 0 | 5.5726 | 11.7625 | 12.38 | 13.03 | 13.714 | 14.434 | 15.1918 | 15.9894 | 16.8288 | 17.7123 | 18.6422 | 19.621 | 20.6511 | 21.7352 | 22.8763 | 24.0773 | 25.3414 | 26.6718 | 28.0721 | 29.5459 | 31.0971 | 32.7296 | 34.448 | 36.2565 | 38.1599 | 20.0817
| Infrastructure O&M | Rs Cr | 0 | 0 | 1.1878 | 2.4719 | 2.5651 | 2.6618 | 2.7621 | 2.8663 | 2.9743 | 3.0864 | 3.2028 | 3.3235 | 3.4488 | 3.5789 | 3.7138 | 3.8538 | 3.9991 | 4.1499 | 4.3063 | 4.4687 | 4.6371 | 4.8119 | 4.9933 | 5.1816 | 5.3769 | 5.5797 | 5.79 | 2.9491
| PBITDA | Rs Cr | 0 | 0 | 83.0547 | 163.0774 | 160.1502 | 157.2149 | 154.2691 | 151.3107 | 148.3372 | 145.3462 | 142.3352 | 139.3013 | 136.2419 | 133.154 | 130.0346 | 126.8804 | 123.6881 | 120.4543 | 117.1753 | 113.8472 | 110.4661 | 107.0278 | 103.5279 | 99.9619 | 96.3248 | 92.6117 | 88.8173 | 54.2065
| Depreciation | Rs Cr | 0 | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256
| PBIT | Rs Cr | 0 | 0 | 54.1203 | 105.0497 | 102.1226 | 99.1873 | 96.2415 | 93.2831 | 90.3096 | 87.3186 | 84.3075 | 81.2737 | 78.2143 | 75.1264 | 72.0069 | 68.8527 | 65.6605 | 95.6031 | 92.324 | 88.996 | 85.6149 | 82.1766 | 78.6767 | 75.1106 | 71.4736 | 67.7605 | 63.966 | 41.7809
| Interest on Loan | Rs Cr | 0 | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on WC Loan | Rs Cr | 0 | 0 | 1.1044 | 2.1981 | 2.1885 | 2.1799 | 2.1724 | 2.166 | 2.1607 | 2.1566 | 2.1537 | 2.152 | 2.1516 | 2.1526 | 2.155 | 2.1588 | 2.1641 | 2.171 | 2.1796 | 2.1899 | 2.2019 | 2.2158 | 2.2316 | 2.2494 | 2.2693 | 2.2915 | 2.3159 | 1.2962
| Profits Before Tax (PBT) | Rs Cr | 0 | 0 | 34.3437 | 54.1432 | 54.7048 | 55.2572 | 55.7982 | 56.3253 | 56.8363 | 57.3286 | 57.7996 | 58.2466 | 58.6668 | 59.0571 | 59.4144 | 59.7356 | 60.0172 | 92.5622 | 90.1444 | 86.8061 | 83.413 | 79.9608 | 76.4451 | 72.8612 | 69.2042 | 65.469 | 61.6502 | 40.4847
| Tax | Rs Cr | 0 | 0 | 5.8934 | 9.291 | 9.3873 | 9.4821 | 9.575 | 9.6654 | 9.7531 | 9.8376 | 9.9184 | 9.9951 | 10.0672 | 10.1342 | 10.1955 | 10.2506 | 10.2989 | 15.8837 | 15.4688 | 14.8959 | 14.3137 | 14.3619 | 22.2852 | 21.4967 | 20.6922 | 19.8705 | 19.0303 | 11.6403
| Profits After Tax (PAT) | Rs Cr | 0 | 0 | 28.4504 | 44.8522 | 45.3175 | 45.7751 | 46.2232 | 46.6599 | 47.0832 | 47.491 | 47.8812 | 48.2515 | 48.5996 | 48.9229 | 49.2189 | 49.485 | 49.7182 | 76.6785 | 74.6756 | 71.9102 | 69.0993 | 65.5989 | 54.1599 | 51.3645 | 48.512 | 45.5985 | 42.6198 | 28.8444
Cash flow statement
| Revenue | Rs Cr | 0 | 0 | 89.815 | 177.3117 | 175.0953 | 172.9066 | 170.7453 | 168.611 | 166.5034 | 164.4221 | 162.3668 | 160.3372 | 158.333 | 156.3538 | 154.3994 | 152.4694 | 150.5635 | 148.6815 | 146.823 | 144.9877 | 143.1753 | 141.3857 | 139.6183 | 137.8731 | 136.1497 | 134.4478 | 132.7672 | 77.2372
| Generation O&M | Rs Cr | 0 | 0 | -5.5726 | -11.7625 | -12.38 | -13.03 | -13.714 | -14.434 | -15.1918 | -15.9894 | -16.8288 | -17.7123 | -18.6422 | -19.621 | -20.6511 | -21.7352 | -22.8763 | -24.0773 | -25.3414 | -26.6718 | -28.0721 | -29.5459 | -31.0971 | -32.7296 | -34.448 | -36.2565 | -38.1599 | -20.0817
| Infrastructure O&M | Rs Cr | 0 | 0 | -1.1878 | -2.4719 | -2.5651 | -2.6618 | -2.7621 | -2.8663 | -2.9743 | -3.0864 | -3.2028 | -3.3235 | -3.4488 | -3.5789 | -3.7138 | -3.8538 | -3.9991 | -4.1499 | -4.3063 | -4.4687 | -4.6371 | -4.8119 | -4.9933 | -5.1816 | -5.3769 | -5.5797 | -5.79 | -2.9491
| Taxes | Rs Cr | 0 | 0 | -5.8934 | -9.291 | -9.3873 | -9.4821 | -9.575 | -9.6654 | -9.7531 | -9.8376 | -9.9184 | -9.9951 | -10.0672 | -10.1342 | -10.1955 | -10.2506 | -10.2989 | -15.8837 | -15.4688 | -14.8959 | -14.3137 | -14.3619 | -22.2852 | -21.4967 | -20.6922 | -19.8705 | -19.0303 | -11.6403
| Change in DSRA | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Income on DSRA | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BG Cost on DSRA | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Change in WC | Rs Cr | 0 | 0 | -25.6789 | 0.19361 | 0.11121 | 0.099367 | 0.087135 | 0.074495 | 0.061424 | 0.047898 | 0.033889 | 0.019371 | 0.0043145 | -0.011311 | -0.027536 | -0.044395 | -0.061924 | -0.080158 | -0.099138 | -0.1189 | -0.1395 | -0.16096 | -0.18335 | -0.20671 | -0.23109 | -0.25655 | -0.28315 | -3.2061
| Cash Flow from Operating Activities | Rs Cr | 0 | 0 | 51.4823 | 153.98 | 150.8741 | 147.8321 | 144.7813 | 141.7198 | 138.6455 | 135.5565 | 132.4506 | 129.3256 | 126.179 | 123.0085 | 119.8115 | 116.5853 | 113.3272 | 104.4905 | 101.6073 | 98.8324 | 96.013 | 92.505 | 81.0594 | 78.2584 | 75.4015 | 72.4847 | 69.5038 | 39.3601
| Capital Expenditure | Rs Cr | 0 | -582.0486 | -660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cash Flow from Investing Activities | Rs Cr | 0 | -582.0486 | -660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
| Commerical Loan - Additions | Rs Cr | 0 | 407.434 | 462.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grant | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equity | Rs Cr | 0 | 174.6146 | 198.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commerical Loan - Repayment | Rs Cr | 0 | 0 | -28.9931 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -57.9862 | -28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Change in WC Loan | Rs Cr | 0 | 0 | 19.2592 | -0.14521 | -0.083411 | -0.074525 | -0.065351 | -0.055871 | -0.046068 | -0.035923 | -0.025417 | -0.014528 | -0.0032359 | 0.0084829 | 0.020652 | 0.033297 | 0.046443 | 0.060119 | 0.074353 | 0.089177 | 0.10462 | 0.12072 | 0.13751 | 0.15503 | 0.17332 | 0.19241 | 0.21236 | 2.4046
| Interest on Debt | Rs Cr | 0 | 0 | -18.6722 | -48.7084 | -45.2293 | -41.7501 | -38.2709 | -34.7917 | -31.3126 | -27.8334 | -24.3542 | -20.875 | -17.3959 | -13.9167 | -10.4375 | -6.9583 | -3.4792 | -0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest on WC Loan | Rs Cr | 0 | 0 | -1.1044 | -2.1981 | -2.1885 | -2.1799 | -2.1724 | -2.166 | -2.1607 | -2.1566 | -2.1537 | -2.152 | -2.1516 | -2.1526 | -2.155 | -2.1588 | -2.1641 | -2.171 | -2.1796 | -2.1899 | -2.2019 | -2.2158 | -2.2316 | -2.2494 | -2.2693 | -2.2915 | -2.3159 | -1.2962
| Cash Flow from Financing Activities | Rs Cr | 0 | 582.0486 | 631.003 | -109.038 | -105.4874 | -101.9908 | -98.4949 | -94.9998 | -91.5056 | -88.0121 | -84.5195 | -81.0278 | -77.5369 | -74.047 | -70.5581 | -67.0701 | -63.5831 | -31.9738 | -2.1052 | -2.1007 | -2.0973 | -2.095 | -2.0941 | -2.0944 | -2.096 | -2.0991 | -2.1035 | 1.1084
Cash Schedule
| Opening cash balance | Rs Cr | 0 | 0 | 0 | 21.9718 | 66.9139 | 112.3006 | 158.1419 | 204.4283 | 251.1482 | 298.2882 | 345.8326 | 393.7638 | 442.0615 | 490.7036 | 539.6651 | 588.9185 | 638.4338 | 688.1779 | 760.6946 | 860.1967 | 956.9284 | 1050.8441 | 1141.254 | 1220.2193 | 1296.3834 | 1369.6889 | 1440.0745 | 1507.4748
| Cash generated during the year | Rs Cr | 0 | 0 | 21.9718 | 44.942 | 45.3867 | 45.8413 | 46.2864 | 46.7199 | 47.14 | 47.5444 | 47.9311 | 48.2978 | 48.6421 | 48.9615 | 49.2534 | 49.5153 | 49.7442 | 72.5166 | 99.5021 | 96.7317 | 93.9157 | 90.4099 | 78.9653 | 76.164 | 73.3055 | 70.3856 | 67.4003 | 40.4685
| Closing Cash Balance | Rs Cr | 0 | 0 | 21.9718 | 66.9139 | 112.3006 | 158.1419 | 204.4283 | 251.1482 | 298.2882 | 345.8326 | 393.7638 | 442.0615 | 490.7036 | 539.6651 | 588.9185 | 638.4338 | 688.1779 | 760.6946 | 860.1967 | 956.9284 | 1050.8441 | 1141.254 | 1220.2193 | 1296.3834 | 1369.6889 | 1440.0745 | 1507.4748 | 1547.9433
Balance Sheet Statement
Assets
| GFA | Rs Cr | 0 | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Accumulated Depreciation | Rs Cr | 0 | 0 | 28.9343 | 86.962 | 144.9896 | 203.0173 | 261.0449 | 319.0726 | 377.1002 | 435.1279 | 493.1555 | 551.1832 | 609.2108 | 667.2384 | 725.2661 | 783.2937 | 841.3214 | 866.1726 | 891.0239 | 915.8751 | 940.7264 | 965.5776 | 990.4288 | 1015.2801 | 1040.1313 | 1064.9826 | 1089.8338 | 1102.2594
| Net Fixed Assets | Rs Cr | 0 | 0 | 1213.6277 | 1155.6001 | 1097.5724 | 1039.5448 | 981.5171 | 923.4895 | 865.4618 | 807.4342 | 749.4065 | 691.3789 | 633.3512 | 575.3236 | 517.2959 | 459.2683 | 401.2406 | 376.3894 | 351.5382 | 326.6869 | 301.8357 | 276.9844 | 252.1332 | 227.282 | 202.4307 | 177.5795 | 152.7282 | 140.3026
| CWIP | Rs Cr | 0 | 582.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Current Assets | Rs Cr | 0 | 0 | 25.6789 | 25.4853 | 25.3741 | 25.2747 | 25.1876 | 25.1131 | 25.0517 | 25.0038 | 24.9699 | 24.9505 | 24.9462 | 24.9575 | 24.9851 | 25.0295 | 25.0914 | 25.1715 | 25.2707 | 25.3896 | 25.5291 | 25.69 | 25.8734 | 26.0801 | 26.3112 | 26.5677 | 26.8509 | 30.057
| DSRA | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cash & Bank Balance | Rs Cr | 0 | 0 | 21.9718 | 66.9139 | 112.3006 | 158.1419 | 204.4283 | 251.1482 | 298.2882 | 345.8326 | 393.7638 | 442.0615 | 490.7036 | 539.6651 | 588.9185 | 638.4338 | 688.1779 | 760.6946 | 860.1967 | 956.9284 | 1050.8441 | 1141.254 | 1220.2193 | 1296.3834 | 1369.6889 | 1440.0745 | 1507.4748 | 1547.9433
| TOTAL ASSETS | Rs Cr | 0 | 582.0486 | 1261.2785 | 1247.9992 | 1235.2471 | 1222.9614 | 1211.133 | 1199.7508 | 1188.8017 | 1178.2706 | 1168.1402 | 1158.3909 | 1149.001 | 1139.9462 | 1131.1995 | 1122.7315 | 1114.51 | 1162.2555 | 1237.0055 | 1309.0049 | 1378.2088 | 1443.9285 | 1498.2259 | 1549.7454 | 1598.4308 | 1644.2217 | 1687.0539 | 1718.3029
Equity and Liabilities
| Equity | Rs Cr | 0 | 174.6146 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686 | 372.7686
| Reserve and Surplus | Rs Cr | 0 | 0 | 28.4504 | 73.3026 | 118.62 | 164.3951 | 210.6183 | 257.2782 | 304.3614 | 351.8524 | 399.7337 | 447.9852 | 496.5847 | 545.5076 | 594.7265 | 644.2115 | 693.9297 | 770.6082 | 845.2839 | 917.1941 | 986.2934 | 1051.8924 | 1106.0523 | 1157.4167 | 1205.9288 | 1251.5273 | 1294.1471 | 1322.9915
| Grants | Rs Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commercial Loan | Rs Cr | 0 | 407.434 | 840.8003 | 782.8141 | 724.8279 | 666.8416 | 608.8554 | 550.8692 | 492.8829 | 434.8967 | 376.9105 | 318.9243 | 260.938 | 202.9518 | 144.9656 | 86.9793 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Working Capital Loan | Rs Cr | 0 | 0 | 19.2592 | 19.114 | 19.0306 | 18.9561 | 18.8907 | 18.8348 | 18.7888 | 18.7528 | 18.7274 | 18.7129 | 18.7097 | 18.7181 | 18.7388 | 18.7721 | 18.8185 | 18.8787 | 18.953 | 19.0422 | 19.1468 | 19.2675 | 19.405 | 19.5601 | 19.7334 | 19.9258 | 20.1382 | 22.5427
| TOTAL LIABILITIES | Rs Cr | 0 | 582.0486 | 1261.2785 | 1247.9992 | 1235.2471 | 1222.9614 | 1211.133 | 1199.7508 | 1188.8017 | 1178.2706 | 1168.1402 | 1158.3909 | 1149.001 | 1139.9462 | 1131.1995 | 1122.7315 | 1114.51 | 1162.2555 | 1237.0055 | 1309.0049 | 1378.2088 | 1443.9285 | 1498.2259 | 1549.7454 | 1598.4308 | 1644.2217 | 1687.0539 | 1718.3029

## IDC Schedule
| Particulars | Units | From | 2025-04-01 | 2025-07-01 | 2025-10-01 | 2026-01-01 | 2026-04-01 | 2026-07-01 | 2026-10-01 | 2027-01-01
|  | 2025-03-31 | To | 2025-06-30 | 2025-09-30 | 2025-12-31 | 2026-03-31 | 2026-06-30 | 2026-09-30 | 2026-12-31 | 2027-03-31
| Is Operational ? | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
| Operational Quarter Number |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2
| Days in Quarter |  |  | 91 | 92 | 92 | 90 | 91 | 92 | 92 | 90
| Year No. |  | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2
| Days in Operations |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 90
| Days in Construction |  |  | 91 | 92 | 92 | 90 | 91 | 92 | 0 | 0
| Proportion of year in operation |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
| Cumulative number of year in operation |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2
Project Phasing as per Erection Schedule
Solar Generation and Transmission
A | Material Phasing Schedule
| Module | % |  | 0% | 0% | 0% | 50% | 50% | 0%
| Floating System | % |  | 0% | 10% | 20% | 20% | 30% | 20%
| Anchoring Mooring System | % |  | 0% | 20% | 60% | 20% | 0% | 0%
| UV/DC/AC/HT Cables | % |  | 0% | 0% | 30% | 30% | 30% | 10%
| Inverter & Inverter Duty Transformer | % |  | 0% | 0% | 0% | 50% | 50% | 0%
| HT Panels & MCR Equipments | % |  | 0% | 0% | 0% | 50% | 50% | 0%
| 220 KV PSS Equipments & Structures | % |  | 0% | 0% | 0% | 50% | 50% | 0%
| Transmission Line | % |  | 0% | 0% | 0% | 50% | 50% | 0%
| 220 KV Bay Activities | % |  | 0% | 0% | 0% | 50% | 50% | 0%
B | Erection & Commissioning Schedule
| Module | % |  | 0% | 0% | 0% | 0% | 0% | 0%
| Floating System | % |  | 0% | 0% | 0% | 20% | 40% | 40%
| Anchoring Mooring System | % |  | 0% | 0% | 0% | 20% | 40% | 40%
| UV/DC/AC/HT Cables | % |  | 0% | 0% | 20% | 40% | 40% | 0%
| Inverter & Inverter Duty Transformer | % |  | 0% | 0% | 0% | 40% | 40% | 20%
| HT Panels & MCR Equipments | % |  | 0% | 0% | 0% | 0% | 50% | 50%
| 220 KV PSS Equipments & Structures | % |  | 0% | 0% | 0% | 0% | 50% | 50%
| Transmission Line | % |  | 0% | 0% | 0% | 0% | 50% | 50%
| 220 KV Bay Activities | % |  | 0% | 0% | 0% | 0% | 50% | 50%
Infrastructure Cost Phasing
C | Civil and Other Construction Cost Schedule | % |  | 0% | 0% | 15% | 15% | 35% | 35%
Project Phasing as per Erection Schedule
Solar Generation and Transmission
A | Material Phasing Cost
| Module | Rs Crore | 329.1921 | 0 | 0 | 0 | 164.5961 | 164.5961 | 0
| Floating System | Rs Crore | 140.0004 | 0 | 14 | 28.0001 | 28.0001 | 42.0001 | 28.0001
| Anchoring Mooring System | Rs Crore | 88.8568 | 0 | 17.7714 | 53.3141 | 17.7714 | 0 | 0
| UV/DC/AC/HT Cables | Rs Crore | 36.5226 | 0 | 0 | 10.9568 | 10.9568 | 10.9568 | 3.6523
| Inverter & Inverter Duty Transformer | Rs Crore | 106.921 | 0 | 0 | 0 | 53.4605 | 53.4605 | 0
| HT Panels & MCR Equipments | Rs Crore | 12.5328 | 0 | 0 | 0 | 6.2664 | 6.2664 | 0
| 220 KV PSS Equipments & Structures | Rs Crore | 65.3967 | 0 | 0 | 0 | 32.6984 | 32.6984 | 0
| Transmission Line | Rs Crore | 9.6122 | 0 | 0 | 0 | 4.8061 | 4.8061 | 0
| 220 KV Bay Activities | Rs Crore | 3.5876 | 0 | 0 | 0 | 1.7938 | 1.7938 | 0
| sub total | Rs Crore | 792.6222 | 0 | 31.7714 | 92.2709 | 320.3494 | 316.5781 | 31.6523
B | Erection & Commissioning Cost
| Module | Rs Crore | 46.4742 | 0 | 0 | 0 | 9.2948 | 18.5897 | 18.5897
| Floating System | Rs Crore | 19.7648 | 0 | 0 | 0 | 3.953 | 7.9059 | 7.9059
| Anchoring Mooring System | Rs Crore | 12.5445 | 0 | 0 | 2.5089 | 5.0178 | 5.0178 | 0
| UV/DC/AC/HT Cables | Rs Crore | 5.1561 | 0 | 0 | 0 | 2.0625 | 2.0625 | 1.0312
| Inverter & Inverter Duty Transformer | Rs Crore | 15.0947 | 0 | 0 | 0 | 0 | 7.5474 | 7.5474
| HT Panels & MCR Equipments | Rs Crore | 1.7693 | 0 | 0 | 0 | 0 | 0.88467 | 0.88467
| 220 KV PSS Equipments & Structures | Rs Crore | 9.2325 | 0 | 0 | 0 | 0 | 4.6162 | 4.6162
| Transmission Line | Rs Crore | 1.357 | 0 | 0 | 0 | 0 | 0.67851 | 0.67851
| 220 KV Bay Activities | Rs Crore | 0.50648 | 0 | 0 | 0 | 0 | 0.25324 | 0.25324
| sub total | Rs Crore | 111.8996 | 0 | 0 | 2.5089 | 20.328 | 47.5558 | 41.5068
A+B | Total | Rs Crore | 904.5218 | 0 | 31.7714 | 94.7798 | 340.6774 | 364.1339 | 73.1592
C | Infrastructure Cost Phasing
| Civil and Other Construction Cost Schedule | Rs Crore | 32.3868 | 0 | 0 | 4.858 | 4.858 | 11.3354 | 11.3354
| Total Solar Generation and Transmission Cost | Rs Crore | 936.9086 | 0 | 31.7714 | 99.6379 | 345.5355 | 375.4693 | 84.4946
Summary of Phasing as per Erection Schedule
| Solar Generation and Transmission Phasing | % |  | 0% | 3.513% | 10.48% | 37.66% | 40.26% | 8.088% |  | as a % of Total Generation & Transmission Cost
| Infrastructure Cost | % |  | 0% | 0% | 15% | 15% | 35% | 35% |  | as % of Total Infrastructure Cost
| Other Cost Phasing | % |  | 0% | 0% | 5% | 5% | 45% | 45%
Phasing of All cost inclusive of Tacx
1 | Capital Expenditure - Generation & Transmission | Rs Cr |  | 0 | 38.0753 | 113.5855 | 408.2725 | 436.3831 | 87.675 | 0 | 0
2 | Capital Expenditure - Infrastructure | 0 |  | 0 | 0 | 2.7887 | 2.7887 | 6.507 | 6.507 | 0 | 0
3 | Capital Expenditure - Other Costs | Rs Cr |  | 0 | 0 | 5.6928 | 5.6928 | 51.2352 | 51.2352 | 0 | 0
| Phasing - Capex | Rs Cr |  | 0 | 38.0753 | 122.067 | 416.754 | 494.1253 | 145.4172 | 0 | 0
4 | IDC | Rs Cr |  | 0 | 0.20095 | 1.0483 | 3.9031 | 8.7516 | 12.2193 | 0 | 0
| Capex incl. IDC | Rs Cr |  | 0 | 38.2762 | 123.1152 | 420.6571 | 502.877 | 157.6365 | 0 | 0
| 0 | 0
| Commerical Loan 1 | % |  | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70%
| Grant | % |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equity | % |  | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30%
| Commerical Loan 1 | Rs Cr |  | 0 | 26.7934 | 86.1807 | 294.46 | 352.0139 | 110.3456 | 0 | 0
| Grant | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equity | Rs Cr |  | 0 | 11.4829 | 36.9346 | 126.1971 | 150.8631 | 47.291 | 0 | 0
| 0 | 0
| IDC Schedule of Commercial Loan | 0
| Opening | Rs Cr |  | 0 | 0 | 26.7934 | 112.974 | 407.434 | 759.4479 | 869.7934 | 855.2969
| Drawdown | Rs Cr |  | 0 | 26.7934 | 86.1807 | 294.46 | 352.0139 | 110.3456 | 0 | 0
| Repayments | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 14.4966 | 14.4966
| Closing | Rs Cr |  | 0 | 26.7934 | 112.974 | 407.434 | 759.4479 | 869.7934 | 855.2969 | 840.8003
| 0 | 0
| Interest Rate | % |  | 6% | 6% | 6% | 6% | 6% | 6% | 6% | 6%
| IDC | Rs Cr |  | 0 | 0.20095 | 1.0483 | 3.9031 | 8.7516 | 12.2193 | 0 | 0
| Interest Charge | Rs Cr |  | 0 | 0 | 0 | 0 | 0 | 0 | 51.7527 | 50.8829
0

## Schedule
| Particulars | Units | Inputs | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
|  |  | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31 | 2031-03-31 | 2032-03-31 | 2033-03-31 | 2034-03-31 | 2035-03-31 | 2036-03-31 | 2037-03-31 | 2038-03-31 | 2039-03-31 | 2040-03-31 | 2041-03-31 | 2042-03-31 | 2043-03-31 | 2044-03-31 | 2045-03-31 | 2046-03-31 | 2047-03-31 | 2048-03-31 | 2049-03-31 | 2050-03-31 | 2051-03-31 | 2052-03-31
| Total Year Counter |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
| Is Operational ? | 26 |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Operational Year Number |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| Days in year |  |  | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366
| Days of Construction |  |  | 0: 365; 1: 183; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0
| Days in Operations |  |  | 0 | 182 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 183
Debt Schedule
Total Project Cost
| Capital Expenditure - Generation & Transmission | Rs Cr |  | 559.9333 | 524.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital Expenditure - Infrastructure | Rs Cr |  | 5.5774 | 13.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital Expenditure - Other Costs | Rs Cr |  | 11.3856 | 102.4704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phasing - Capex | Rs Cr |  | 576.8963 | 639.5425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IDC | Rs Cr |  | 5.1523 | 20.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capex incl. IDC | Rs Cr |  | 582.0486 | 660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Commercial Loan | % |  | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70%
Commerical Loan Schedule
| Opening | Rs Cr |  | 0 | 407.434 | 840.8003 | 782.8141 | 724.8279 | 666.8416 | 608.8554 | 550.8692 | 492.8829 | 434.8967 | 376.9105 | 318.9243 | 260.938 | 202.9518 | 144.9656 | 86.9793 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Addition | Rs Cr |  | 407.434 | 462.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repayments | Rs Cr |  | 0 | 28.9931 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 57.9862 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 407.434 | 840.8003 | 782.8141 | 724.8279 | 666.8416 | 608.8554 | 550.8692 | 492.8829 | 434.8967 | 376.9105 | 318.9243 | 260.938 | 202.9518 | 144.9656 | 86.9793 | 28.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Rate | % | bar: 0 to 26
| IDC | Rs Cr |  | 5.1523 | 20.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Charge | Rs Cr |  | 0 | 18.6722 | 48.7084 | 45.2293 | 41.7501 | 38.2709 | 34.7917 | 31.3126 | 27.8334 | 24.3542 | 20.875 | 17.3959 | 13.9167 | 10.4375 | 6.9583 | 3.4792 | 0.86979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Depreciation Schedule
CWIP Schedule | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opening | Rs Cr |  | 0 | 582.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Addition | Rs Cr |  | 582.0486 | 660.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capitalised | Rs Cr |  | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Closing | Rs Cr |  | 582.0486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book Depreciation | 0 | 0
GFA Schedule
| Opening GFA | Rs Cr |  | 0 | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Additions | Rs Cr |  | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256
| Accumulated depreciation | Rs Cr |  | 0 | 28.9343 | 86.962 | 144.9896 | 203.0173 | 261.0449 | 319.0726 | 377.1002 | 435.1279 | 493.1555 | 551.1832 | 609.2108 | 667.2384 | 725.2661 | 783.2937 | 841.3214 | 866.1726 | 891.0239 | 915.8751 | 940.7264 | 965.5776 | 990.4288 | 1015.2801 | 1040.1313 | 1064.9826 | 1089.8338 | 1102.2594
| Closing GFA | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Max depreciation | Rs Cr |  | 0 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058
| Opening NFA | Rs Cr |  | 0 | 0 | 1213.6277 | 1155.6001 | 1097.5724 | 1039.5448 | 981.5171 | 923.4895 | 865.4618 | 807.4342 | 749.4065 | 691.3789 | 633.3512 | 575.3236 | 517.2959 | 459.2683 | 401.2406 | 376.3894 | 351.5382 | 326.6869 | 301.8357 | 276.9844 | 252.1332 | 227.282 | 202.4307 | 177.5795 | 152.7282
| Addition - NFA | Rs Cr |  | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256
| Closing - NFA | Rs Cr |  | 0 | 1213.6277 | 1155.6001 | 1097.5724 | 1039.5448 | 981.5171 | 923.4895 | 865.4618 | 807.4342 | 749.4065 | 691.3789 | 633.3512 | 575.3236 | 517.2959 | 459.2683 | 401.2406 | 376.3894 | 351.5382 | 326.6869 | 301.8357 | 276.9844 | 252.1332 | 227.282 | 202.4307 | 177.5795 | 152.7282 | 140.3026
Accumulated Depreciation
| Opening | Rs Cr |  | 0 | 0 | 28.9343 | 86.962 | 144.9896 | 203.0173 | 261.0449 | 319.0726 | 377.1002 | 435.1279 | 493.1555 | 551.1832 | 609.2108 | 667.2384 | 725.2661 | 783.2937 | 841.3214 | 866.1726 | 891.0239 | 915.8751 | 940.7264 | 965.5776 | 990.4288 | 1015.2801 | 1040.1313 | 1064.9826 | 1089.8338
| Depreciation during the year | Rs Cr |  | 0 | 28.9343 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 24.8512 | 12.4256
| Closing | Rs Cr |  | 0 | 28.9343 | 86.962 | 144.9896 | 203.0173 | 261.0449 | 319.0726 | 377.1002 | 435.1279 | 493.1555 | 551.1832 | 609.2108 | 667.2384 | 725.2661 | 783.2937 | 841.3214 | 866.1726 | 891.0239 | 915.8751 | 940.7264 | 965.5776 | 990.4288 | 1015.2801 | 1040.1313 | 1064.9826 | 1089.8338 | 1102.2594
Depreciation (Tax)
GFA Schedule
| Opening GFA | Rs Cr |  | 0 | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Additions | Rs Cr |  | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 95.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accumulated depreciation | Rs Cr |  | 0 | 95.553 | 191.106 | 286.6591 | 382.2121 | 477.7651 | 573.3181 | 668.8711 | 764.4242 | 859.9772 | 955.5302 | 1051.0832 | 1146.6362 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893 | 1242.1893
| Closing GFA | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Max depreciation | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
Accelerated Depreciation
GFA Schedule
| Opening GFA | Rs Cr |  | 0 | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562
| Additions | Rs Cr |  | 0 | 1242.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Depreciation | Rs Cr |  | 0 | 0 | 621.281 | 0 | 497.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accumulated depreciation | Rs Cr |  | 0 | 0 | 621.281 | 621.281 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058 | 1118.3058
| Closing GFA | Rs Cr |  | 0 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562 | 1242.562

## Sheet1 (hidden)
Changes Made |  | Earlier | New
APC | % | 0% | 0.75%
O&M Cost | Lakh/MW | 3 | 5.5
O&M Cost Escalation | % | 3.2% | 5.25%
Loan tenure | Years | 12 | 15
ROE |  | Blend of MAT and Corporate | First 20 Years MAT and the Corporate
Total Project Cost | Rs Crore | 1045 | 1068
Inverter Cost- | Rs Crore | 19.7 | 25.7
Transformer Cost | Rs Crore | 16 | 33.1
Environment Mitigation Cost | Rs Crore | 0 | 1.2
LCOE |  | 4.09 | 4.75